## TOTAL
REVISED | 2001-05-24
MONTHLY ACTIVITY AT A GLANCE
FOR
2001-03-19
TRANSMISSION PROJECTS
UTILITY | TOTAL PROJECTS REPORTED | TOTAL PROJECTED EXPENDITURES FOR REPORTED PROJECTS | NEW PROJECTS | ESTIMATED EXPENDITURES FOR NEW PROJECTS | COMPLETED PROJECTS | ESTIMATED EXPENDITURES OF COMPLETED PROJECTS | TOTAL ACTIVE PROJECTS | ESTIMATED EXPENDITURES FOR ACTIVE PROJECTS | ESTIMATED EXPENDITURES FOR ACTIVE PROJECTS FROM PREVIOUS MONTH
BRZ | 14 | 35197138 | 0 | 0 | 1 | 600000 | 9 | 34597138 | 35197138
CPL | 19 | 118193931 | 0 | 0 | 1 | 0 | 16 | 118193931 | 118193931
EGS | 18 | 33109758 | 1 | 0 | 0 | 0 | 10 | 33109758 | 33099758
EPE | 4 | 10311439 | 0 | 0 | 0 | 0 | 4 | 10311439 | 10311439
HLP | 35 | 130979700 | 1 | 720000 | 2 | 2030000 | 33 | 128949700 | 129694700
LCRA | 11 | 108428758.21 | 0 | 0 | 0 | 0 | 11 | 108428758.21 | 108428758.21
MVEC | 4 | 2913000 | 0 | 0 | 1 | 0 |  | 2913000 | 2913000
PEC | 3 | 9229859 | 0 | 0 | 0 | 0 | 3 | 9229859 | 9229859
SPEC | 1 | 855003 | 0 | 0 | 0 | 0 |  | 855003 | 855003
SPS | 3 | 39912828 | 0 | 0 | 1 | 2157719 | 2 | 37755109 | 39912828
STEC* | 92 | 81615400 | 2 | 2147000 | 0 | 0 |  | 81615400 | 79468400
SWEPCO | 4 | 5680000 | 0 | 0 | 0 | 0 | 7094000 | 5680000 | 5680000
TXU | 65 | 206075132 | 2 | 903872 | 8 | 2695517 | 57 | 203379615 | 205171260
WTU | 2 | 95522744 | 0 | 0 | 0 | 0 | 2 | 95522744 | 95522744
TOTAL | 275 | 878024690.21 | 6 | 3770872 | 14 | 7483236 | 7094147 | 870541454.21 | 873678818.21

## BRZ
RIGHT-OF-WAY
PROJECT NUMBER. | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
90007 | New Hope Loop | Johnson & Somervell Counties | CCN Docket # 17370 | 2001-03-02 | 2001-06-15 | 3915750 |  |  | 15% | 7.7 miles | 795 MCM ACSR | wood or concrete single pole |  |  | 35 ft. feathered | 7.7 miles | Docket # 17370 |  |  | 3915750
96019 | Shady Grove to West Weatherford | Parker County | Construct 69 KV line adjacent to existing 138 KV line. | 2001-03-02 | 2001-07-15 | 1906750 |  |  | 10% | 4.0 miles | 4/0 ACSR | single wood pole |  |  | 100 ft. | 4.0 miles | Docket # 22314 |  |  | 1906750
86029 | Gibbons Creek to Roans Prairie | Grimes County | Construct 138 KV line from Texas Municipal Power Agency's Gibbons Creek generating plant to Roans Prairie Substation | 2001-06-01 | 2001-10-15 | 3218650 |  |  | 0% | 10.0 miles | 795 MCM ACSR | single steel, wood &/or concrete poles |  |  | 100 ft. | 10.0 miles | Docket # 22206 |  |  | 3218650
98024 | Crowley Substation & Transmission Line | Johnson County | Construct double circuit 138 KV line from the proposed substation terminating at a switch to be constructed in Brazos' existing Joshua to Egan 138 KV line. | 2001-03-15 | 2001-09-15 | 2099700 |  |  | 0% | 2.5 miles | 795 ACSR | single steel, wood &/or concrete poles |  |  | 100 ft. | 2.5 miles | Docket # 22367 |  |  | 2099700
95038 | Mountain Springs Substation & Transmission Line | Cooke County | Construct 5.2 miles of DC line from existing Salem Switch to Salem Sub line to new Mountain Springs substation. | 2001-05-01 | 2001-09-01 | 2883200 |  |  | 0% | 5.2 miles | 795 MCM ACSR | single steel, wood &/or concrete poles |  |  | 70-100 ft. | 5.2 miles | Docket # 20422 | Survey work beginning |  | 2883200
96095 | Salem Loop | Cooke County | Construct 6.3 miles 138 KV transmission line from existing Salem Sub to existing Woodbine Sub. | 2001-05-01 | 2001-09-01 | 2686300 |  |  | 0% | 6.3 miles | 795 MCM ACSR | single steel, wood &/or concrete poles |  |  | 70-100 ft. | 6.3 | Docket # 20516 | Final Order issued |  | 2686300
90012 | Liveoak to North Texas Rebuild | Parker County | Rebuild the Liveoak to North Texas line with 138 KV 795 MCM ACSR construction | 2000-03-05 | 2001-05-15 | 1452300 |  |  | 5% | 7.7 miles | 795 MCM ACSR | single steel, wood &/or concrete poles | 60 ft. | 7.7 miles |  |  | 25.101(c)(2)(C)(v) |  |  | 1452300
9960013 | Weatherford Re-route | Parker County | Re-route approx. 5600 feet of transmission line for Southwest Ford dealership | 2001-02-28 | 2001-03-15 | 600000 | 646250 | 8% | 100% | .96 miles | 795 MCM ACSR | 3 steel freestanding, 1 concrete dead-end, 9 concrete tangents | 60 ft. | 0.96 | 60 ft. | .96 miles | 25.101(c)(2)(C)(iii) |  | 600000
99012 | TinTop -Granbury | Hood and Parker | Reconductor 14.4 miles of line with 795 MCM 138 kV construction | 2001-05-01 | 2001-05-25 | 2546650 |  |  | 0% | 14.3 | 795 MCM | Single pole wood | 60 ft. | 14.3 miles |  | 14.3 miles | 25.101(c)(2)(C)(ii) |  |  | 2546650
00002 | Booneville to Hearne | Robertson & Brazos County | Rebuilding of approx. 23 miles of 138 kV 795 MCM line from existing Booneville sub. to existing Hearne sub. | 2001-06-01 | 2001-08-15 | 4841000 |  |  | 0% | 23 miles | 795 MCM | Single Pole Concrete | 60 ft. | 23 miles |  | 23.0 miles | 25.101(c)(2)(C)(ii) |  |  | 4841000
00010 | Rhome to Bridgeport East | Wise County | Reconductor 15.5 miles of 477 MCM conductor with 795 MCM conductor | 2001-02-15 | 2001-06-01 | 3429250 |  |  | 0% | 15.5 miles | 795 MCM | Wood H-frame | 60 ft. | 15.5 miles |  | 15.5 miles | 25.101(c)(2)(C)(ii) |  |  | 3429250
00009 | Bowie to Sunset | Montague County | Reconductor 138 kV H-frame with 795 MCM conductor | 2001-02-15 | 2001-06-01 | 2324750 |  |  | 0% | 10.5 miles | 795 MCM | Single Pole Concrete | 60 ft. | 10.5 miles |  | 10.5 miles | 25.101(c)(2)(C)(ii) |  |  | 2324750
88022 | Iola to Roans Prairie | Grimes County | Uprate the line section to 212 degrees F rating (construct for 138 kV) | 2001-06-01 | 2001-10-01 | 2482950 |  |  | 0% | 12.5 miles | 795 MCM | Single Pole Concrete | 60 ft. | 12.5 miles |  | 12.5 miles | 25.101(c)(2)(C)(ii) |  |  | 2482950
9960019 | DalMac Re-route | Dallas County | Re-route approx. 3000 feet of transmission line for landowner | 2001-03-01 | 2001-06-15 | 809888 |  |  | 0% | 0.56 miles | 336 ACSR | Single Pole Steel | 60 ft. | 0.56 miles |  | 0.56 miles | 25.101(c)(2)(C)(iii) |  |  | 809888
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 600000 | 34597138 | 35197138
NEW
EXISTING
CONSTRUCTION COSTS

## CPL
RIGHT-OF-WAY
PROJECT NUMBER. | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS |  | ESTIMATED
21071518 | Coleto Creek-Pawnee 345 kV | Goliad & Kennedy Counties | New 345 kV line between Coleto Creek Power Station and new STEC Pawnee Switching Station | 2001-03-01 | 2002-03-01 | 37887000 |  |  |  | 104.6 mi | Double Crkt 1590 MCM bundled | Steel Lattice Towers |  |  | 160 ft | 52.3 mi |  | Docket #21741 |  | 37887000
21074391 | Chase Field Line Tap | Bee County, Tx | Construct 4.2 miles of new 69kv 795 MCM 26/2 ACSR transmission line from the Chase Field Substation to a Tap point on the Skidmore to Beeville transmission line near Beeville Tx. using single pole construction | 2001-10-01 | 2002-02-01 | 1052000 |  |  |  | 4.2 | 795 MCM ACSR | Concrete Pole with davit arms |  |  | 60 ft | 4.2 miles |  | Full CCN-Scheduled to be filed 3/15/00; CCN delayed until discussions with landowners can be held, status report due 7/10/00. Working with the landowners at this time. We will refile 12/1/00 Should know by 4/10/00 whether hearing will be required |  | 1052000
21886771 | Dupont SS-Whitepoint SS 138 kV-2nd CRKT | San Patricio County, TX | Install Second 795 MCM ACSR circuit on the existing couble circuit steel structures between Dupont SS and Whitepoint SS | 2000-05-15 | 2000-08-01 | 718000 |  |  | 95% | 8.2 Mi | 795 MCM ACSR | Existing Double Circuit Steel Structures | Centerline Defined | 8.2 Mi |  |  | SUB R. 25.101(c)(2)(C)(ii) | Existing double circuit tower and circuit were installed in 1973 Filed on Interim |  | 718000
21886729 21886701 | Nueces Bay/Portland/Whitepoint 138 kV | San Patricio County, TX | Install 2.7 Miles of double circuit concrete poles (2) 795 MCM 138 kV line from Lon Hill-Rincon 138 kV to the Whitepoint Switching Station | 2001-01-20 | 2001-04-01 | 1178965 |  |  |  | 5.4 Mi | (2) 795 MCM ACSR | Double Circuit single pole concrete structures |  |  | 80' | 2.7 Mi |  | Docket #2234 Approved |  | 1178965
21886673 21924122 | Lon Hill/Rincon-Whitepoint 138 kV | San Patricio County, TX | Install 3.2 miles of double circuit concrete pol (2) 795 MCM 138 kV line from Lon Hill-Rincon 138 kV Line to Whitepoint Switching Station | 2001-01-01 | 2001-03-15 | 1528458 |  |  |  | 6.4 Mi | (2) 795 MCM ACSR | Double Circuit single pole concrete structures |  |  | 80' | 3.2 Mi |  | Docket #22312 Approved |  | 1528458
21723155 21924105 | Lon Hill/STP-Whitepoint 345 kV | San Patricio County, TX | Install 10.1 Miles of double circuit steel single pole (2) 795 MCM 345 kV from Lon Hill-Stp Line to Whitepoint Switching Station | 2000-11-15 | 2001-04-01 | 6661038 |  |  | 50% | 20.2 Mi | (2) 795 MCM ACSR | Double Circuit single pole concrete structures |  |  | 100 | 10.1 Mi |  | Docket #22294 Approved |  | 6661038
21884738 | Highway 9-Arcadia 69 kV Upgrade | Corpus Christi, Nueces County | Convert existing 69 kV line from Highway 9 to Acradia Substation to 138 kV and reconductor with 1590 MCM ACSR. 1.1 Miles of wood single pole will be replaced with either concrete or steel single poles. | (10/15/00) | 2001-03-19 | 1381000 |  |  | 75% | 5.8 Mi | 1590 MCM ACSR | 4.7 mi steel double circuit, 1.1 miles steel single poles | Centerline Defined | 5.8 Mi |  |  | SUB R. 25.101(c)(2)(C)(ii) | Revised the estimate |  | 1381000
21722984 | Citgo NOP-Lon Hill 138 kV | Corpus Christi, Nueces County | Construct a new 138 kV transmission line from Citgo NOP to Lon Hill Sub in three secgments, 1.6 miles of single circuit single pole, 2.8 miles of double circuit single pole and 10. Miles of single circuit single pole. | 2001-03-01 | 2001-11-01 | 17406178 |  |  |  | 14.7 | 2-795 kcmil ACSR |  |  |  | 60' | 11.9 Mi |  | Docket #22338 Approved |  | 17406178
21822970 | Citgo NOP-Nueces Bay 138 kV cable | Corpus Christi, Nueces County | Install 0.6 miles of underground cable from Citgo NOP substation to Nueces Bay Substation in conduit, 138 kV, 2-1000 kcmil Cu per phase in 4 conduits. | 2001-03-01 | 2001-11-01 | 10009940 |  |  |  | 0.6 Mi | 2-1000 kcmil Cu per phase in 4 Conduits | Cable |  |  | 20 | 0.6 Mi |  | Docket #22340 Approved |  | 10009940
21723002 | Lon Hill Power Station to Nueces Bay Power Station | Corpus Christi, Nueces County | Install a new 138 kV line in four segments from Lon C Hill Power Plant to Nueces Bay Power Plant. Segment 1-5.4 miles of double circuit single pole, Segment 2-0.2 miles of single circuit single pole, Segment 3-3.2 Miles of single circuit single pole, Segment 4-8.4 miles of double-circuit single pole, all constructed with 2-795 kcmil ACSR. | 2001-03-01 | 2001-11-01 | 22629986 |  |  |  | 17.2 | 2-795 kcmil ACSR | Single Pole With Davit Arm |  |  | 60' and 100' | 8.8 Mi |  | Docket #22339, CCN Approved |  | 22629986
21722914 | Citgo NOP-Hwy 9 138 kV Line | Corpus Christi, Nueces County | Construct 0.6 miles of new 138 kV transmission and rebuild 1.06 miles of 69 kV to 138 kv between Citgo North Oak Park Substation and Highway 9 Substation. Constructed on single poles with 1590 mcm ACSR. | 2001-06-15 | 10//01 | 10004657 |  |  |  | 1.66 | 1590 MCM ACSR | Steel Or Concrete poles single or doubel circuit |  | 1.06 Mi | 50 to 75 ' | 0.66 |  | Docket #21838 Approved |  | 10004657
21884756 | Arcadia-Southside 69 kV Upgrade | Corpus Christi, Nueces County | Convert Existing 69 kV line on wood single pole to 138 kV from Arcadia to Southside Station. Three spans of double circuit wood H frame into the Southside Substation will be rebuilt with steel single pole double circuiut | 2000-08-15 | 2000-09-15 | 700944 |  |  | 90% | 14,630 ft | 795 MCM | Existing wood single pole or steel single pole double circuit | Centerlined defined and public right of way | 14,630 ft |  |  | SUB R. 25.101(c)(2)(C)(ii) | Revised the estimate |  | 700944
21884765 | Southside-Holly 69 kV Upgrade | Corpus Christi, Nueces County | Convert existing 69 kV line on wood single pole to 138 kV from Holly Substation to Southside Substation. Three spans of double circuit wood H frame in the Southside Station will be rebuilt with steel or concrete single pole double circuit | (8/24/00) | 2001-09-15 | 434765 |  |  | 90% | 1.83 mi | 795 MCM | Existing wood single pole or steel single pole double circuit | Centerline Defined | 1.83 Mi |  |  | SUB R. 25.101(c)(2)(C)(ii) | Revised the estimate |  | 434765
21884824 | Arcadia Westside 69 kV Upgrade | Corpus Christi, Nueces County | Convert existing 69 kV line on wood H frame double circuit structures to double circuit steel and or concrete 138 kV structures and reconductor with 1590 MCM ACSR | (10/15/2000) | 2000-12-15 | 1084000 |  |  | 70% | 2.97 MI | 1590 MCM ACSR | Double Circuit single pole concrete or steel structures | Centerlined defined and public right of way | 2397 Mi |  |  | SUB R. 25.101(c)(2)(C)(ii) | Revised the estimate |  | 1084000
22170041 | Mines Road-North Laredo Switch Tap 138kV Reconductor | Webb County, Tx | Reconductor and rebuild approximately 2 miles of existing 138kV transmission line from Mines Road Substation to the tap point for the North Laredo Switch Station. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2000-11-01 | 2000-12-20 | 520000 |  |  | 20% | 2 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 2 mi |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in CPL single certified service area and a portion is located in Medina Electric Cooperative single certified service area |  | 520000
22169991 | Milo-Mines Road 138kV Reconductor | Webb County, Tx | Reconductor and rebuild approximately 3 miles of existing 138kV transmission line from Milo Substation to Mines Road Substation. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2000-12-10 | 2001-02-10 | 724000 |  |  | 0% | 3 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 3 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) & Sub Rule 25.101(c) (2) (C) (iv) | The line is located in CPL single certified service area. A short portion of the line wil be altered to accommodate the industrial park development to avoid future encroachments. |  | 724000
22169942 | Laredo Plant-Milo 138kV Reconductor | Webb County, Tx | Reconductor and rebuild approximately 3 miles of existing 138kV transmission line from Laredo Plant to Milo Substation. The old line is 336 MCM ACSR conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2001-02-15 | 2001-05-01 | 758000 |  |  | 20% | 3 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 3 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in CPL single certified service area. |  | 758000
22151899 | Bates-Garza 138 kV line Reconductor | Hildago County, Tx | Reconductor and rebuild approximately 12 miles of existing 138 kV transmission line from Bates Power Plant to Sructure #87 on the Bates/Garza 138 kV transmission line. The existing line is 336 MCM Aluminum conductor on wood "H" frame structures and will reconductored with 795 MCM ACSR on steel poles.Single Circuit | 2000-10-01 | 2000-12-31 | 2645000 |  |  | 90% | 12 Mi | 795 MCM ACSR & 7 #8 Alumoweld shield wire | Steel Single pole | Centerline Defined | 12 Mi |  |  | Sub Rule 25.101(c) (2) ( C )(ii) | The line is located in a CPL single certified service area. Added from September Interim report |  | 2645000
21739138 | East Harrison- Harlingen #1 69 kV Line Reconductor | Cameron County, Tx | Reconductor and rebuild approximately 4.0 miles of existing 69kV transmission line from East Harrison Substation to Harlingen #1 Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conductor on steel poles | 2001-01-22 | 2001-04-06 | 870000 |  |  | 30% | 4.0 mi. | 795 MCM & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 4.0 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | Line located in CPL single certified service area. Added by way of 12/00 interim report. |  | 870000
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 118193931 | 118193931
NEW
EXISTING
CONSTRUCTION COSTS

## EPE
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | CONSTRUCTION COST |  | VAR (%) | COM (%) | LENGTH | CONDUCTOR | STRUCTURE | RIGHT-OF-WAY |  |  |  | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
[13 empty] | EXISTING |  | NEW
[6 empty] | ESTIMATED | FINAL | [5 empty] | W | L | W | L
1135 | Montwood Substation | El Paso County | Install 3.5 miles of new 115kV circuit on existing 'H' frame structures. Construct 1.5 miles of new 115kV circuit on steel structures. Construct new (Montwood) 115/23.9kV, 30 MVA substation. | 2000-04-14 | 2001-06-15 | 3445000 |  |  | 80 | 5 miles | 954 ACSR | 75' H-frame structures (Existing) 90' galvanized steel, single pole structures (new) | 150' | 3.5 miles | 100' 150' | 0.5 mile 1.0 mile | 20943 | A 24Kv feeder will be energized on or about 4/15/01. Construction to complete the project will continue through June. The permanent transformer is expected to ship 5/11/01. Shipping and installation and field testing is expected to take an additional 5 weeks. |  | 3445000
0909 | Montwood to Horizon 115 kV Line | El Paso County | Construct 10.51 miles of new 115 kV circuit on single pole steel structures. Upgrade existing Horizon Substation from 69/13.8/12 MVA to 115/13.8/30 MVA substation. An existing 69kV line (0.93 mile in length) currently operating at 13.8kV will be rebuilt. This portion of line will be constructed to accomodate an additional 115kV circuit in the future. | 2001-05-07 | 2001-11-09 | 4342238 |  |  |  | 10.53 miles | 954 ACSR | 90' galvanized steel single pole structures utilizing delta configuration for single circuit. 90'-95' single pole galvanized steel structures utilizing vertical construction will be used on segment designated for double circuit. | Existing 0.94 miles of line located in Horizon Blvd. R.O.W. under permit issued by TxDot. |  | 100' 60' 15' | 8.17 mile 0.13 mile 1.29 mi. (overhang) | 22574 | Second phase of planned 115kV system. Line will extend from Montwood Sub to existing Horizon Substation located in Horizon City. |  | 4342238
0970 | Wrangler to Horizon 115kV Upgrade (Horizon to Sparks non-exempt portion) | El Paso County | As part of the overall Eastside Expansion Project, the existing 69kV line serving Horizon substation from Wrangler, will be upgraded to 115kV to complete a loop from Caliente to Wrangler via Sparks substation. The project is divided into two segments, Horizon to Sparks and Sparks to Wrangler. The majority of the project will involve rebuilding and upgrading existing facilities. This particular segment involves construction of 0.77 mile of new line to connect Sparks to existing facilities along I-10 and the line being rebuilt from Horizon. | 2001-05-07 | 2002-01-11 | 1786846 |  |  |  | 0.77 miles | 954 ACSR | 90' galvanized steel single pole structures. | 200' | 0.72 miles |  |  | 22574 | Existing Horizon tap will be rebuilt at 115kV from Horizon sub west to Nonap Rd. A new line will be built in existing EPE R.O.W. paralleling Nonap Rd. to the proposed Sparks Substation site. Lines will be constructed from Sparks substation to tie to existing lines paralleling I-10. |  | 1786846
0970 | Wrangler to Horizon 115kV Upgrade (Horizon to Sparks exempt portion) | El Paso County | As part of the overall Eastside Expansion Project, the existing 69kV line serving Horizon substation from Wrangler, will be upgraded to 115kV to complete a loop from Caliente to Wrangler via Sparks substation. The project is divided into two segments, Horizon to Sparks and Sparks to Wrangler. The majority of the project will involve rebuilding and upgrading existing facilities. This particular segment involves rebuilding 3.15 miles of line from Horizon Substation to the new Sparks tap. The line will be upgraded from 69kV to 115kV. | 2001-11-12 | 2002-01-11 | 737355 |  |  |  | 3.15 miles | 954 ACSR | 90' galvanized steel single pole structures. | 1.0 miles of line located in Horizon Blvd. R.O.W. under TxDot Permit; 0.15 mile in 60' EPE ROW; 2.0 miles in 30' easement |  |  |  | 25.101(c)(2)(C)(ii) | Existing facilities to be rebuilt maintaining present centerline. 65' wood pole structures and 336.4 ACSR conductor to be replaced. |  | 737355
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 10311439 | 10311439

## EGS
[8 empty] | VAR. (%) | COM (%) |  |  |  | RIGHT-OF-WAY
[6 empty] | CONSTRUCTION COSTS | [6 empty] | EXISTING |  | NEW
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL |  |  | Length in Miles | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
CEA TS3372 | Cut in Entergy Gulf States 138 kV line 419 for new Onalaska Substation | Livingston County, Texas | SHECO has requested that EGS cut in its new Onalaska Substation from EGS's 138/239 kV Line 419. This is a customer owned substation and SHECO has provided an easement for the two 80 ft. wide by approximately 270 ft. long ROW's to make the cut in. | 1999-06-14 | 1999-12-31 | 80862 | 80862 |  | 95% | 535 ft. | 2-649.5 MCM ACAR | Concrete Single Pole Structures |  |  | 80 ft. | 535 ft. | Project No. 20662 Subst R. §25.101 (c)(2)(C)(i) | Waiting on customer to complete substation work | 0 | 80862
| Construct Double Circuit 138 kV lines from Entergy's South Beaumont Bulk to Exxon/Mobil's Customer owned Station | Jefferson County, Texas | Construct double circuit 138 kV (3.5 miles) with fiber optic | 2001-07-01 | 2001-10-01 | 5395700 | 5395700 |  | 0% | 3.5 | 954 ACSR | Concrete and Steel Single Pole Structures | 150 ft. | 2 miles | 80 ft. | 1.5 miles | Subst. R. §25.101(c)(2)(C)(i) | Reimbursable by customer. Lines to new customer owned substation | 0 | 5395700
CEA TL 3308 CEA TS 3567 | Cut in Entergy's 138 kV Line 172 for new Entergy owned Oilla Substation | Orange County, Texas | EGS proposes to construct a new 138/18.8 kV substation to be called Oilla Substation. The substation will be owned by EGS and will be used to alleviate current feeder overload in the area | 2000-04-01 | 2000-11-01 | 360244 | 360244 |  | 99% | 100' |  | Two - 2 pole dead end switch structures |  |  | 100 ft. | 100 ft. | Subst. R. §25.101(c)(2)(C)(i) | Line is cut-in. Waiting on charges to accumulate to close out. This substation is immediately adjacent to the existing line. Consequently, a single span is needed to connect. | 0 | 360244
CEA TL 3295 | Cut in Entergy Gulf States 138 kV Line 442 for new customer owned Liberty Substation. | Liberty County, Texas | The City of Liberty has requested EGS cut in the city's new Liberty Substation from EGS 138 kV Line 442. This substation is located immediately adjacent to EGS's right of way and also immediately adjacent to Liberty's existing Liberty National Substation. | 2000-04-15 | 2000-11-15 | 184639 | 184639 |  | 95% | 50' | 1024.ACAR | Install 1 steel H-Frame and 2 - (3) Pole deadend steel structures |  |  | 50 ft. | 50 ft. | Subst. R. §25.101(c)(2)(C)(i) | The cost of this work is to be reimbursed by the customer. Waiting on Customer. | 0 | 184639
CEA TL 3327 | Raise 69kV Line 466 to accommodate Interstate HWY 10 Overpass | Jefferson, County Texas | Increase the height of six (6) structures in their approximate existing locations to accommodate modifications to an existing IH10 overpass that will result in the overpass being higher off the ground. | 2000-10-01 | 2000-11-21 | 45000 | 45000 |  | 99% | 0.22 | 795 MCM AL | Replace 6 wooden structures with 6 concrete structures |  |  |  |  | Subst R. §25.101 (c)(2)(C)(v) | Requested by State Highway Department. Delay start per State. Line is in service. Waiting on Charges to accumulate. | 0 | 45000
| Construct 138 kv Line from New Switching Station to Sempra Plant | Liberty, Harris and Montgomery Counties, Texas | Construct 138kV Line from new switching station to Sempra's customer owner station | 2002-05-15 | 2002-09-15 | 7300000 | 7300000 |  | 0% | 10.3 Miles | 795 MCM AL | Concrete Pole Single Structures | 150 ft. | 10.3 miles |  |  | Subst. R. §25.101(c)(2)(C)(i) | Reimbursable by customer (Sempra) | 0 | 7300000
| Construct 2 - 138 kV lines from Eastgate Substation to Sempra Plant | Liberty County, Texas | Construct 2 - 138 kv lines from Eastgate Substation to Sempra Plant | 2002-05-15 | 2002-09-15 | 485000 | 485000 |  | 0% | .6 miles | 795 MCM AL | Concrete Pole Single Structures |  |  | 150 ft. | 0.6 miles | Subst. R. §25.101(c)(2)(C)(i) | Reimbursable by customer (Sempra) | 0 | 485000
CEA 3382 | Relocate existing take-off structures for Line 418-A at Jacinto Substation to allow for future expansion | Liberty County, Texas | Replace two single pole structures with one three pole structure | 2000-10-30 | 2001-01-30 | 35000 | 35000 |  | 80% | 50' | 649 ACAR Bundled | Concrete Pole |  |  |  |  | Subst. R. §25.101(c)(2)(C)(ii) |  | 0 | 35000
CEA 3383 | Relocate existing take-off structures for Line 524 at Jacinto Substation to allow for future expansion | Liberty County, Texas | Replace and relocate one single pole structure with one three pole structure | 2000-10-30 | 2001-01-03 | 35000 | 35000 |  | 80% | 0 | 395 ACAR | Concrete Pole |  |  |  |  | Subst. R. §25.101(c)(2)(C)(ii) |  | 0 | 35000
CEA 3381 | Relocate existing take-off structures for Line 568 at Jacinto Substation to allow for future expansion | Liberty County, Texas | Replace two single pole structures with one three pole structure | 2000-10-30 | 2001-01-03 | 35000 | 35000 |  | 80% | 0 | 795 ACSR Bundled | Concrete Pole |  |  |  |  | Subst. R. §25.101(c)(2)(C)(ii) |  | 0 | 35000
CEA TL 4151 | Upgrade Line 455 from Jasper to Newton Substation by bundling conductor | Jasper and Newton Counties | Replace 53 structures and reconductor 15.8 miles | 2001-03-15 | 2001-06-01 | 2215585 | 2215585 |  | 0% | 15.8 | 336 ASCR Bundled | Concrete Pole Single Structures |  | 15.8 |  | 0 | Subst. R. §25.101(c)(2)(C)(ii) | Construction package issued to field for review. | 0 | 2215585
CEA TL 3256 | Upgrade Line 568 from China to Jacinto by bundling conductor | Jefferson, Hardin and Liberty Counties | Replace 25 structures and reconductor 50 miles | 2000-12-11 | 2001-05-01 | 5290000 | 5290000 |  | 95% | 50 | 795ACSR bundled | Concrete Pole H-Frame Structures |  | 50 |  |  | Subst. R. §25.101(c)(2)(C)(ii) | Conductor 100% strung, need to replace two additional structures and replace four arms | 0 | 5290000
CEA TL 4148 | Upgrade Line 569 from Laon Sub. to Lewis Creek by bundling conductor | Montgomery County | reconductor 475 feet of conductor | 2000-12-01 | 2000-12-15 | 50400 | 50400 |  | 99% | 0.1 | 666 ACSR | [5 empty] | Subst. R. §25.101(c)(2)(C)(ii) |  | 0 | 50400
CEA TL 3426 | Rebuild Line 587 conroe Bulk to Lewis Creek by bundling conductor | Montgomery County | Replace estiamted 95 poles and bundle 17.8 miles | 2001-12-01 | 2002-04-01 | 5916415 | 5916415 |  | 0% | 17.8 | 649 ACAR | Replace wooden structures with concrete or steel |  | 17.8 miles |  |  | Subst. R. §25.101(c)(2)(C)(ii) | Work associated with Line 820 project | 0 | 5916415
CEA TL 3425 | Rebuild Line 403 Goslin to Proposed Forest Site | Montgomery County | Replace estimated 41 poles and bundle 2.9 miles | 2001-12-01 | 2002-04-01 | 1388064 | 1388064 |  | 0% | 2.9 | 666ACSR | Replace wooden structures with concrete or steel |  | 2.9 miles |  |  | Subst. R. §25.101(c)(2)(C)(ii) | Work associated with Line 820 project | 0 | 1388064
CEA TL3422 | Cut in Entergy Gulf States 69 kV line 62 for new substation | Jefferson County, Texas | EGS proposes to construct a new 69/13.8 kV substation to be called Pansy Substation. The substation will be owned by EGS and will be used to alleviate current feeder overload in the area | 2001-03-01 | 2001-05-01 | 140000 | 140000 |  | 0% | 0.1 |  | Install 2 DLA-DEP-C type structures, remove wooden poles |  |  |  | 0.1 miles | Subst. R. §25.101(c)(2)(C)(i) |  | 0 | 140000
CEA TL 3423 | Cut in Entergy Gulf States 69 kV line 500 for new substation | Orange County, Texas | EGS proposes to construct a new 69/13.8 kV substation to be called West Orange Substation. The substation will be owned by EGS and will be used to alleviate current feeder overload in the area | 2001-03-01 | 2001-05-01 | 255849 | 255849 |  | 0% | 0.1 |  | Install 3 DLA-DEP-C type structures, remove wooden poles |  |  |  | 0.1 miles | Subst. R. §25.101(c)(2)(C)(i) |  | 0 | 255849
CEA TL3429 | Line 820 - 138 kV Transmission line between Conroe Bulk and Forest Substations | Montgomery County | Construct a 138 kV Transmission Line 820 from Conroe Bulk to the site of the new Forest Substation to support load growth in Montgomery County, Texas | 2001-10-01 | 2002-04-01 | 3837000 | 3837000 |  | 0% | 5.6 | 666 ACSR Bundled | Concrete or Steel Single Ples Structures |  |  | 80 ft. | 5.6 miles | PUCT Docket No. 23429 | The CCN application includes the new Forest Substation whick is scheduled to be constructed in October 2007. The construction costs shown herein include the transmission line only and does not include the cost of the Forest Substation. | 0 | 3837000
CEA TL3433 | Rebuild 138kV Line 492 Cow Bulk to Sabine |  | Bundle 0.06 miles 649 ACAR conductor | 2001-03-20 | 2001-03-31 | 60000 | 50000 |  | 0% | 0.06 | 649 ACAR Bundled | [7 empty] | 0 | 60000
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 0
[19 empty] | 0 | 33109758 | 33109758

## LCRA
PROJECT NUMBER. | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | CONSTRUCTION COSTS |  | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | RIGHT-OF-WAY |  |  |  | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
[13 empty] | EXISTING |  | NEW
[6 empty] | ESTIMATED | FINAL | [5 empty] | W | L | W | L
244601 | Flatonia-Yoakum | Fayette, Lavaca, De Witt Counties | Overhaul (maintenance) of an existing 69 kV transmission line and adding lightning protection, shield wires, arresters and modifying existing structures | 2000-05-22 | 2001-03-01 | 682200 |  |  | 99% | 27.67 | 3x1-2/0 ACSR "Quail ". 3x1-4/0 ACSR "Penguin", 3x1-336 ACSR "Linnet" | H-frame, Single Pole | 100 ft, CL | 27.67 | - | - | 25.101(c)(2)(C)(ii) | Complete Pending Final Costs |  | 682200
103280 | Hays Generation New 345 kV (Zorn to Kendall T227) | Hays County | New second 345 kV circuit on existing towers to connect Zorn to the Hays Energy Switchyard | 2000-10-01 | 2000-10-27 | 481022 |  |  | 99% | 2.6 | 3x2-715 ACSR "Redwing" (Bundled) | Lattice Tower | 175 ft | 2.6 | - | - | 21199 |  |  | 481022
1001710 | Salem Walk-Barton | Travis County | Reconductor/bundle existing circuit with 3x2-795 ACSR "Drake", part of 138 kV circuit from HiCross to Marshall Ford | 2000-02-21 | 2000-03-13 | 496000 |  |  | 99% | 3.8 | 3x2-795 ACSR "Drake" (bundled) | Lattice Tower, Steel H | 100 ft | 3.8 | - | - | 25.101(c)(2)(C)(ii) | Complete Pending Final Billing from Construction Contractor |  | 496000
425101 | Lockhart-Dump Hill | Caldwell County | Add a second circuit at 138 kV and upgrade existing 69 kV circuit by rebuilding an existing transmission line | 2001-04-01 | 2001-06-15 | 662300 |  |  | 0% | 1.6 | 6x1-795 MCM ACSR "Drake" | Steel or Concrete H-frame, Single Pole | CL, 40ft, 60 ft | 0.96 | CL, 40ft, 60 ft | 0.64 | 22369 |  |  | 662300
425102 | Dump Hill-Mendoza | Caldwell County | Upgrade existing circuit by rebuilding and reconductoring with 3x1-795 ACSR "Drake" and upgrading to 138 kV | 2001-01-02 | 2001-04-01 | 1278700.21 |  |  | 52% | 7.6 | 3x1-795 MCM ACSR "Drake" | Steel or Concrete or Wood H-frame and existing lattice tower | CL | 7.6 | - | - | 25.101(c)(2)(C)(ii) |  |  | 1278700.21
1001742 | McCarty Lane-Redwood | Hays County | Upgrade existing circuit by rebuilding and reconductoring/bundling with 3x2- 795 ACSR from McCarty Lane Substation to Redwood Substation | 2001-03-01 | 2001-06-01 | 778336 |  |  | 0% | 2.31 | 3x2-795 MCM ACSR "Drake" (bundled) | H-frame | 100 ft | 2.31 | - | - | 25.101(c)(2)(C)(ii) |  |  | 778336
1001743 | Redwood-San Marcos | Hays County | Upgrade existing circuit by rebuilding and reconductoring/bundling with 3x2- 795 ACSR from Redwood Substation to San Marcos Substation | 2001-06-05 | 2001-10-01 | 796355 |  |  | 0% | 2.52 | 3x2-795 MCM ACSR "Drake" (bundled) | H-frame | 100 ft | 2.58 | - | - | 25.101(c)(2)(C)(ii) |  |  | 796355
1001857 | Cuero-Yoakum | DeWitt County | Upgrade existing circuit by modifying or replacing certain structures to provide additional ground clearance for operation of existing 795 ACSR conductors at 200 degrees Fahrenheit with a capacity of 920 amperes (220 MVA) from Cuero to Yoakum | 2000-11-01 | 2001-01-10 | 350000 |  |  | 99% | 13.84 | 3x1-795 MCM ACSR "Drake" | Wood H-frame (primarily) | 100 ft | 13.84 | - | - | 25.101(c)(2)(C)(ii) |  |  | 350000
1001776 & 1001840 | Kunitz-Wink | Culberson, Reeves, Loving, Winkler Counties | New 138 kV transmission line from wind plant at Kunitz to TXU Wink Substation | 2001-09-01 | 2002-11-01 | 30212829 |  |  | 0% | 101.5 | 3x2-795 MCM ACSR "Drake" | Single Pole & H-frame | - | - | 100-160 ft | 101.5 | 22762 | CCN Pending |  | 30212829
1002197 | Sterling/Mitchell County Line-New Twin Buttes Station-Existing Red Creek Station-Coleman/Brown County Line | Coleman, McCulloch, Concho, Tom Green, Coke, Concho and Sterling Counties | New 345 kV transmission line, designed double circuit, one circuit installed with a double-circuit split into the new Twin Buttes Station | 2001-06-01 | 2003-06-30 | 71965000 |  |  | 0% | 144.7 | 3x2-1590 MCM ACSR "Falcon" | Lattice Tower | - | - | 160 ft | 139.2 | 22798 | CCN Pending |  | 71965000
1001895 | Bastrop Energy Switchyard - Garfield Switchyard | Bastrop County | New 345 kV transmission line | 2001-07-01 | 2001-11-01 | 726016 |  |  | 0% | 0.4 | 3x2-795 MCM ACSR "Drake" | Single Pole, H-frame, Multi-pole | - | - | 100 ft | 0.4 | 23192 | CCN Pending |  | 726016
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 108428758.21 | 108428758.21

## MVEC
RIGHT-OF-WAY
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | COM (%) | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS |  | ESTIMATED
4921 | Aderhold Transmission Line | Hidalgo | 1.6 Mile Double Circuit 138kv Transmission Line | est 2/05/2001 | est 3/30/2001 | 760000 |  |  | 0% | 1.6 miles | 795 ACSR | Single pole - double circuit - concrete pole with steel davit arms |  |  | 23', 27', 50', 50', 50', 50' | 930', 1040', 660', 1710', 3480', 660' | 17432 | Line Design and Easement acquistion continuing at this time |  | 760000
1972336 | Kenaf Plant | Willacy | 6.5 Miles 138kv Transmission Line | Delayed - May not be built | Delayed - May not be built | 1550000 |  |  | 0% | 6.5 miles | 795 ACSR | Single pole - concrete pole with steel davit arms |  |  | 25' | 3600' | 19577 | No change during the past month - MVEC has stopped all work related to this line until the Cooperative has assurances that the new load is going to materialize |  | 1550000
1971909 | Weslaco Switch Station | Hidalgo | 0.4 Miles Double Circuit 138 kV Transm. Line | 8/21/2000 | est 9/22/2000 | 603000 |  |  | 100% | 0.4 miles | 795 ACSR | Single pole - double circuit - concrete pole with steel davit arms | 0 | 0 | 40' | 2180' | 21110 | Construction was completed on 9-19-2000. Line is in service, but work order is not closed |  | 603000
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 2913000 | 2913000
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING

## PEC
RIGHT-OF-WAY
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | COM (%) | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS |  | ESTIMATED
0
CR900910Y | WIMBERLEY TO DRIPPING SPRINGS | WIMBERLEY, DRIPPING SPRINGS, HAYS COUNTY | CONSTRUCT 138KV FROM WIMBERLEY TO DRIPPING SPRINGS | UNKNOWN | UNKNOWN | 2269408 | N/A | N/A | N/A | 13.9 MI. | 795 ACSR DRAKE | SINGLE WOOD POLE | N/A | N/A | 100' | 13.9 MI. | PUC# 11014 | LAST 750' INTO WIMBERLEY SUB WILL BE UNDERGROUND |  | 2269408
0
0
0
XE974659Y | FRIENDSHIP TO MANCHACA | NORTHERN HAYS AND SOUTHERN TRAVIS COUNTY | CONSTRUCT 138KV FROM FRIENDSHIP TO MANCHACA, NEW SUBSTATION IN CIRCLE C | UNKNOWN | UNKNOWN | 6863881 | N/A | N/A | N/A | 7.8 MI. | 795 ACSR DRAKE | SINGLE POLE STEEL-CONCRETE | N/A | N/A | 80' | 7.8 MI. | PUC# 18389 | 3700 FEET ACROSS Circle C Golf Course will be underground |  | 6863881
0
0
0
XE996949Y | RELOCATION OF 138kV CREEK @ DRIFTWOOD | RUTHERFORD TO DRIPPING SPRINGS | RELOCATE 138kV LINE IN SUBDIVISION | UNKNOWN | UNKNOWN | 96570 | N/A | N/A | N/A | 2105' | 795 ACSR DRAKE | SINGLE WOOD POLE | 100' | 1900' | 100' | 2105' | EXEMPT | PROPERTY OWNER IS PAYING FOR RELOCATION |  | 96570
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 9229859 | 9229859
NEW
EXISTING

## RHLP
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | CONSTRUCTION COSTS |  | VAR.(%) | % COM | LENGTH | CONDUCTOR | STRUCTURE | RIGHT-OF-WAY |  |  |  | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
[13 empty] | EXISTING |  | NEW
[6 empty] | ESTIMATED | FINAL | [5 empty] | W | L | W | L
190 | SIENNA | Ft. Bend County | 138 kV Service to a Utility-owned substation greater than 2 spans away from an existing transmission line | 2001-04-01 | 2001-09-01 | 4288000 |  |  | 0% | 5.4 | 1433.6 ACSS | Steel Towers, Steel Poles, and Concrete Poles | N/A | N/A | 75ft.-243ft. | 2.7mi | PUC Docket 20624 | Final Order signed 11/1/00. PCR filed 11/20/00. |  | 4288000
144 | Galveston | Harris and Galveston Counties | Build New 138 kV Circuit | 2000-08-08 | 2001-07-01 | 11110000 |  |  | 15% | 28.2 | 795 AAC/ACSR, 2000 CU | Steel Towers, Concrete Poles, Underground Cable | 100ft.-150ft. | 21.8mi | 20ft.-100ft., street | 6.4mi | PUC Docket 20887 | Final Order signed 4/12/00. PCR filed 5/22/00. |  | 11110000
243.1 | SHELDN (Generation Interconnection) | Harris County | 345 kV Service to Customer-owned SHELDN Metering Point from Ckts. 74F and 75C; 138 kV Partial Rebuild of Ckt. 08; Upgrade of 69 kV Ckt. 61B to 138kV | 2000-02-21 | 2001-08-01 | 15400000 |  |  | 55% | 20.2 | 2167 ACSR, 795 ACSR/AAC | Steel Poles, Steel Towers, Concrete Poles | Street, 100ft.-150ft. | 6.83mi; 1.67mi; 4.77mi | 100ft.-150ft. | 0.21mi | 25.101(c)(2)(C)(i) and (ii) |  |  | 15400000
300 | Eastside - Polk | Harris County | Relocation of Underground 138 kV Ckt. 91 to avoid an encroachment by the City of Houston's George R. Brown Convention Center expansion. | 2001-01-03 | 2001-07-01 | 2595000 |  |  | 31% | 0.6 | 2500 KCMIL CU XLPE Cable | Underground Cable | NA | NA | Street | 0.6mi | 25.101(c)(2)(C)(iv) |  |  | 2595000
367 | Greens Bayou - Lychem | Harris County | Partial Rebuild and Reconductor of 138 kV Ckts. 08F & 03F and Partial Rebuild of 69 kV Ckt. 38B | 2000-08-15 | 2001-04-15 | 3260000 |  |  | 85% | 11.3 | 959.6 ACSS, 795 AAC | Concrete Poles, Steel Towers, Wooden H-Frames | Street, 100ft.-150ft. | 7.2mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 3260000
371 | Campbell-White Oak | Harris County | Reconductor and Partial Rebuild of 138 kV Ckts. 09I and 21H | 2001-01-03 | 2001-03-30 | 844000 |  |  | 70% | 11.5mi | 959.6 ACSS | Steel Towers | 150ft.-250ft. | 5.8mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 844000
223 | Alvin - LaMarque | Brazoria, Galveston Counties | 69 kV Partial Rebuild and Partial Reconductoring of Ckt. 53B | 2000-05-25 | 2001-04-01 | 1400000 |  |  | 92% | 20.7 | 4/0 ACSR, 397.5 ACSR, 795 AAC | Wooden H-Frames, Concrete/Steel/Wood Poles, Steel Towers | 22ft. - 106ft., Street | 20.7mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 1400000
298 | Longhorn Glass (FDLITY) | Harris County | 138 kV Service to Customer-owned substation from Ckt. 21K | 2000-07-13 | 2000-12-19 | 1530000 | 1423472 | -7% | 100% | 2.6 | 795 ACSR | Concrete Poles, Steel Poles, Steel Towers | N/A | N/A | POHA R.O.W., HCFCD R.O.W. | 1.3mi | 25.101(c)(2)(C)(i) | Last time to report. Customer paid $740,982 toward the cost of the project. | 1530000
315 | King - North Belt | Harris County | 345 kV Reconductor and Partial Rebuild of Ckts. 97B & 99G | 2000-11-27 | 2002-05-01 | 6900000 |  |  | 15% | 22mi | 959.6 ACSS | Steel Towers | 150ft. | 11mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 6900000
362 | North Belt - T.H. Wharton | Harris County | 345 kV Reconductor and Partial Rebuild of Ckt. 97A | 2000-08-05 | 2002-02-02 | 4230000 |  |  | 90% | 10mi | 959.6 ACSS | Steel Towers | 150ft. | 10mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 4230000
248 | Baytown Energy Center (CHAMBR) | Chambers County | 345 kV Service to Customer-owned CHAMBR Metering Point from Ckt. 97C | 2000-12-11 | 2001-03-31 | 1055000 |  |  | 96% | 0.1mi | 1433.6 ACSS | Steel Towers | N/A | N/A | 280ft. | 0.02mi | 25.101(c)(2)(C)(i) |  |  | 1055000
270 | Austin Substation | Harris County | 138 kV Service to Utility-owned Substation within 2 spans of Ckt. 90 | 2000-12-18 | 2001-03-13 | 900000 |  |  | 99% | 0.07mi | 2500 KCMIL HPFF Cable | Underground Cable | Street | Street | N/A | N/A | 25.101(c)(2)(C)(i) | Construction Complete. |  | 900000
337 | Eastside - University | Harris County | 138 kV Reconductor and Partial Rebuild of Ckt. 91B | 2000-09-30 | 2000-12-19 | 500000 | 1326071 | 165% | 100% | 2.9mi | 959.6 ACSS | Steel Towers, Steel Poles | 50ft., Street | 2.9mi | N/A | N/A | 25.101(c)(2)(C)(ii) | Last time to report. Higher labor costs were incurred because multiple outages were required and scope of work to install special conductor was underestimated. Construction access was also more difficult than expected. | 500000
349 | H.O.Clarke - Dunlavy | Harris County | 69 kV Partial Rebuild and Reconductor of Ckt. 40A | 2001-01-02 | 2001-08-31 | 680000 |  |  | 60% | 9.3mi | 1433.6 ACSS, 795 AAC | Concrete Poles, Steel Towers | 130ft.-500ft., Street | 9.3mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 680000
379 | Clinton - Harrisburg | Harris County | 69 kV Bundling and Partial Rebuild of Ckt. 33C | 2001-04-17 | 2001-05-31 | 1100000 |  |  | 0% | 6.3mi | 795 AAC, 1433.6 ACSS | Concrete Poles, Steel Towers, Wood Poles | 70ft., Street | 6.3mi | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 1100000
238 | Kuykendahl Substation | Harris County | 345 kV Service to Utility-owned Substation within 2 spans of Ckts. 74B & 75B | 2001-05-01 | 2001-06-01 | 200000 |  |  | 0% | 0.11mi | 1590 ACSR | Concrete Poles | 100ft., Substation Property | 0.06mi | NA | NA | 25.101(c)(2)(C)(i) |  |  | 200000
333 | H.O.Clarke - Karsten | Harris, Fort Bend, and Brazoria Counties | 69 kV Partial Rebuild of Ckt. 53E | 2000-10-30 | 2001-04-15 | 335000 |  |  | 90% | 24.4mi | 795 ACSR, 397 ACSR, 4/0 AAAC | Steel Towers, Concrete Poles, Wood Poles | 17ft. - 462ft. | 24.4mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 335000
333 | Texas Gulf - West Columbia | Wharton, Matagorda, and Brazoria Counties | 138 kV Partial Rebuild of Ckt. 04F | 2000-11-13 | 2001-07-15 | 364600 |  |  | 5% | 27.5mi | 795 AAC, 795 ACSR | Steel Towers, Wooden H-Frames, Concrete Poles | 50ft-250ft. | 27.5mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 364600
408 | Cedar Bayou - King | Chambers, Liberty, and Harris Counties | 345 kV Reconductor and Partial Rebuild of Ckts. 97C & 99G | 2001-03-20 | 2002-05-01 | 24000000 |  |  | 0% | 57.2mi | 1433.6 ACSS | Steel Towers | 230ft.-370ft. | 28.6mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 24000000
119 | Boltex (TAYLOR) | Harris County | 138 kV Service to Customer-owned substation from Ckt. 84C | 2001-04-15 | 2001-05-01 | 75000 |  |  | 0% | 0.01mi | 795 AAC | Steel Pole | NA | NA | 50-100ft. | 0.1mi | 25.101(c)(2)(C)(i) |  |  | 75000
339 | Channel Energy Center (DEPWTR) | Harris County | 345 kV Service to Customer-owned DEPWTR Metering Point from Ckts. 68 & 69; Partial Rebuild and Reconductor of 138 kV Ckts. 70D & 77A | 2001-04-01 | 2001-10-01 | 33000000 |  |  | 0% | 20.8 | 959.6 ACSS | Steel Poles, Steel Towers | 75ft-500ft | 7.9mi | 0ft.-150ft. | 1mi | 25.101(c)(2)(C)(i) and (ii) |  |  | 33000000
398 | Crosby - King | Harris County | 138 kV Partial Reconductor and Bundle of Ckt. 86E | 2001-04-01 | 2001-12-31 | 2755000 |  |  | 0% | 17.6mi | 959.6 ACSS, 795 ACSR | Steel Towers | 80ft.-500ft. | 17.6mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 2755000
413 | Greens Bayou - Lydell | Harris County | 138 kV Partial Reconductor of Ckts. 70C & 70D | 2001-06-01 | 2002-03-01 | 287000 |  |  | 0% | 2.0mi | 959.6 ACSS | Steel Poles, Steel Towers | Power Plant Property, 50-130ft. | 1.5mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 287000
241 | Westview Drive | Harris County | 138 kV Relocation of Ckts. 73A & 80D within 200 feet of existing facilities as requested by the City of Houston for extension of Westview Dr. | 2001-02-14 | 2001-03-13 | 78800 |  |  | 99% | 0.10mi | 795 AAC | Concrete Poles | 50ft. | 0.10mi | NA | NA | 25.101(c)(2)(C)(v) | Construction Complete. Actual cost to be reimbursed by City of Houston. |  | 78800
305 | Cedar Bluff (HARGRV) | Harris and Liberty Counties | 138 kV Service to Customer-owned HARGRV Metering Point from Ckt. 66E | 2002-06-01 | 2002-08-31 | 4149000 |  |  | 0% | 8.4mi | 959.6 ACSS | Concrete Poles, Steel Towers | NA | NA | 150ft. | 4.2mi | PUC Docket 23577 | CCN filed 1/18/01. Pending PUCT approval. |  | 4149000
426 | Port of Houston Woodhouse Terminal | Harris County | 138 kV Relocation of Ckt. 20C at the request of and the expense of the Port of Houston in existing Right-of-Way | 2001-02-26 | 2001-02-28 | 35000 |  |  | 0% | 0.07mi | 4/0 ACSR | Concrete Poles | Street | 0.07mi | NA | NA | 25.101(c)(2)(C)(iii) | Actual cost to be reimbursed by Port of Houston. |  | 35000
449 | Metro Light Rail | Harris County | 138 kV Alteration of Ckts. 06K & 08B within 200 feet of existing facilities as requested by Metro for Light Rail Construction | 2001-04-16 | 2001-05-01 | 30300 |  |  | 0% | 0.1mi | 795 AAC & 2000 AAC | Concrete Pole | 100ft. | 0.09mi | NA | NA | 25.101(c)(2)(C)(v) | Actual cost to be reimbursed by Metro. |  | 30300
445 | Akzo Nobel (NOBEL_) | Harris County | 138 kV Service to Customer-owned substation from Ckt. 21C | 2001-06-01 | 2001-07-01 | 55000 |  |  | 0% | 0.06mi | 795 AAC | Steel Tower | NA | NA | 115ft. | 0.03mi | 25.101(c)(2)(C)(i) | Actual cost to be reimbursed by Akzo Nobel Polymer Chemicals, L.L.C. |  | 55000
332 | Tiki Island Mobile Substation | Galveston County | 138 kV Service to Utility-owned Substation within 2 spans of Ckt. 01 | 2001-04-01 | 2001-04-16 | 25000 |  |  | 0% | 0.02mi | 795 ACSR | Concrete Pole | Substation Property | 0.02mi | NA | NA | 25.101(c)(2)(C)(i) |  |  | 25000
333 | T.H. Wharton - White Oak | Harris County | 69 kV Partial Rebuild of Ckt. 29A | 2001-03-23 | 2001-04-30 | 283000 |  |  | 0% | 12.4mi | 795 AAC | Wood Poles | 20ft.-570ft., Street | 12.4mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 283000
433 | MetroNexus (MINMAX) | Harris County | 138 kV Service to Customer-owned substation from Ckt. 73A | 2001-05-15 | 2001-06-15 | 170000 |  |  | 0% | 0.04mi | 795 AAC | Steel Pole | NA | NA | 50ft.-100ft. | 0.02mi | 25.101(c)(2)(C)(i) | Actual cost to be reimbursed by MetroNexus/Southwest, L.L.C. |  | 170000
467 | Liverpool Substation | Brazoria County | 138 kV Service to Utility-owned substation within 2 spans of Ckt. 04C | 2001-04-15 | 2001-05-04 | 21000 |  |  | 0% | 0.04mi | 795 AAC | Wood Poles | 100ft., Substation Property | 0.02mi | NA | NA | 25.101(c)(2)(C)(i) |  |  | 21000
472 | Crosby - Atascocita | Harris County | 138 kV Reconductor and Partial Rebuild of Ckt. 66E | 2001-04-01 | 2001-12-31 | 6204000 |  |  | 0% | 12.7mi | 959.6 ACSS | Concrete Poles, Steel Towers | 47ft.-300ft. | 12.7mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 6204000
474 | Kingwood - Humble | Harris County | 138 kV Reconductor and Partial Rebuild of Ckt. 66E | 2001-09-01 | 2002-03-01 | 2400000 |  |  | 0% | 7.7mi | 959.6 ACSS | Concrete Poles, Steel Towers | 80ft.- 100ft. | 7.7mi | NA | NA | 25.101(c)(2)(C)(ii) |  |  | 2400000
439 | Hyde Park - Dunlavy | Harris County | 69 kV Rebuild and Reconductor of Ckt. 32A | 2001-07-23 | 2001-10-01 | 720000 |  |  | 0% | 1.5 mi | 1433 ACSS | Concrete Poles, Steel Poles | Street | 1.5mi | NA | NA | 25.101(c)(2)(C)(ii) | New Project. |  | 720000
[19 empty] | 2030000 | 128949700 | 130979700

## STEC
RIGHT-OF-WAY
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | COM (%) | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
701.2026, 801.2025 & 801.4013 | Industrial Park | Wharton | Install 69 kV Arresters. And split transformer | 1/2001 | 6/2001 | 26000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Transformer received on site. |  | 26000
700-7081 | Bay City | Matagorda | Install MW to Bay City Office | 6/2000 | 12/2000 | 50000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 50000
701.4012 &801.4011 | Oaks | Atascosa | Install Interval Metering. | 1/2001 | 6/2001 | 50000 |  |  | 20% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 50000
701.4028 & 801.4027 | Carancahua | Matagorda | Install Interval Metering. | 1/2001 | 6/2001 | 50000 |  |  | 20% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 50000
797-2023, 797-2027 & 897-2026 | Calliham South Sw. | Live Oak | Install MW, SCADA and MOD | 1/1997 | 12/2000 | 80000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Closing out. |  | 80000
798-2014 | Loyola | Kleburg | Install Mw to Ricardo | 1/1998 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
799-6019 | JEC Office | Victoria | Install MW and SCADA to Edna | 2/1999 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-1026, 700-4127 & 800-4126 | Industrial | Wharton | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-1020 | Pioneer | Colorado | Install communications | 2/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-4011, 700-6012, 700-4131, 700-1024 & 800-4130 | Van Vleck | Matagorda | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
797-2103 | Leona | Duval | Install MW to San Diego | 2/1997 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-4133, 700-1025 & 800-4132 | Clemville North | Matagorda | Install equipment required for substation automation, & Communications | 8/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-6101, 700-4137, 700-1027 & 800-4136 | Inez | Victoria | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-6045 | Sodville | San Patricio | Install MW & SCADA to W Sinton Sw. | 4/2000 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out.
797-2032 | George West 138 kV | Live Oak | Install MW and SCADA to S. Call. Sw | 1/1997 | 12/2000 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
799-6020 | Edna | Jackson | Install MW and SCADA to El Toro | 2/1999 | 1/2001 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-9154, 700-6155, 700-4152 & 800-4152 | West Sinton | San Patricio | Install MW and SCADA to Sodville | 4/2000 | 1/2001 | 150000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 150000
700-4209, 700-6211, 700-9210 &800-4208 | Calliham North | McMullen | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-6050, 700-4135 & 800-4134 | El Toro | Jackson | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-1008, 700-6009, 799-4050 & 899-4049 | Orange Grove 69 kV | Jim Wells | Install equipment required for substation automation, SCADA & Communications | 1/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-2044 | Danevang 138kV | Wharton | Install MW & SCADA to Clemville | 4/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-9206, 700-4205, 700-6207, & 800-4204 | Calliham South | Live Oak | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-6187, 700-9186, 700-4185 & 800-4184 | Corpus Christi | Nueces | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-9242, 700-6243, 700-4241 & 800-4240 | Choke Canyon | Live Oak | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-6263, 700-9262 & 800-4260 | Danevang 69kV | Wharton | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-6175, 700-9174, 700-4173 & 800-4172 | George West | Live Oak | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-4257, 700-6259, 700-9258 & 800-4256 | Plainview | Wharton | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 150000
700-6231, 700-9230, 700-4229 & 800-4228 | McFaddin | Victoria | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-6100 & 700-6049 | El Toro Sw. | Victoria | Install MW and SCADA to El Toro | 4/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-6159, 700-4157, 700-9158 & 800-4156 | Central | Nueces | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-6267, 700-9266, 700-4265 & 800-4264 | Clemville South | Matagorda | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4169, 700-9170, 700-6171 & 800-4168 | Olmos | Bee | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-6191, 700-9190, 700-4189 & 800-4188 | Simmons | Live Oak | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4177, 700-9178, 800-4176 &700-6179 | Bonnie View | Refugio | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-6239, 700-9238,700-4237 & 800-4236 | Charco | Goliad | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-9250, 700-6251, 700-4249 & 800-4248 | Ganado | Jackson | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4221, 700-9222, 700-6223 & 800-4220 | Kamey | Calhoun | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4181, 700-6183, 700-9182 & 800-4180 | Riverside | Nueces | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-9146, 700-6147, 700-4145 & 800-4144 | Kenedy | Karnes | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4165, 700-6167, 700-9166 & 800-4164 | Sandia | Duval | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-1023, 700-4139 & 800-4138 | Schroeder | Goliad | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-2331 | Sharyland | Hidalgo | Install SCADA Metering | 9/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 150000
700-4197, 700-6199, 800-4196 & 700-9198 | Bee Prison | Bee | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-1028, 700-4129 &800-4128 | Charlotte | Atascosa | Install equipment required for substation automation, & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-4213, 700-6215, 700-9214 & 800-4212 | Coy City | Karnes | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-9246, 700-4245, 700-6241 & 800-4244 | Lolita | Jackson | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
797-4067 | Refugio | Refugio | Install MW & SCADA to Goliad | 2/97 |  | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-6151, 700-4149, 700-9150 & 800-4148 | Refugio | Refugio | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-6235, 700-4233, 700-9234 & 800-4232 | Twin Pines | Victoria | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 75% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 150000
700-4094, 700-2095 & 800-4093 | Oaks 138 kV | Atascosa | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-6143, 700-9142, 700-4141 & 800-4140 | Olivia | Calhoun | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-6219, 700-4217, 700-9218 & 800-4216 | Palacios | Matagorda | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-4201, 700-9202, 700-6203 & 800-4200 | Tilden | McMullen | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-4225, 700-6227, 700-9226 &800-4224 | Van Humble | Jackson | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-6195, 700-4193, 700-9194 & 800-4192 | West George West | Live Oak | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-9162, 700-6163, 700-4161 & 800-4160 | Taft | San Patricio | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 150000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 150000
700-2002 & 800-2001 | Install & remove poles in the 138 kV system. | system wide | Install new pole in the 138 kV system. | 1/2000 | 12/2003 | 150000 |  |  | 44% | [7 empty] | 25.101 (c) (2) (C ) (i) | In Progress. |  | 150000
701-2030 | Clemville South Tie | Matagorda | Construct single circuit 69 kV line. | 6/2001 | 12/2001 | 160000 |  |  | 2% | 3 mile | #795 AAAC | Single pole. |  |  | 50 | 3 | pre-CCN | Ordered bid for fly over maps. |  | 160000
700-9102 | Pioneer | Colorado | Purchase substation from CP&L | 6/2000 | 2/2001 | 180000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (B) | Closing out. |  | 180000
700-4253, 700-6255, 700-9254 & 800-4252 | Round Mott | Wharton | Install equipment required for substation automation, SCADA & Communications | 8/2000 | 6/2001 | 180000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 180000
701.2033, 701.4034 & 801.2032 | West Sinton | San Patricio | Install 69 kV Arresters and add 5MVA transformer. | 2/2001 | 6/2001 | 182000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Transformer received on site. |  | 182000
701.2024, 701.4017 & 801.2023 | Franklin's Camp | Brazoria | Install 69 kV Arresters and add 5MVA transformer. | 1/2001 | 6/2002 | 182000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Equipment on order. |  | 182000
701.4016 & 801.4015 | Inez | Victoria | Upgrade to 7.5 MVA transformer. | 1/2001 | 6/2002 | 182000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Equipment on order. |  | 182000
700-6051 & 700-6052 | MW from El Campo to Industrial Park substation. | Wharton | MW equipment for El Campo and Industrial Park substations. | 5/2000 | 12/2000 | 200000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 200000
799-2099 | MW repeater at Crossroads | Jackson | MW Repeater Equipment & tower at Crossroads substation site. | 11/1999 | 12/2000 | 200000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communication building installed |  | 200000
797-4064 | MW from Leona comm. Site to San Diego substation. | Duval | MW equipment for San Diego substations. | 2/1997 | 3/2001 | 200000 |  |  | 85% | [7 empty] | 25.101 (c) (2) (C ) (i) | Communications building installed. |  | 200000
700-6091 & 700-6089 | MW Hop for CORUS substation & Riverside substation. | Nueces | MW Hop equipment at Calallen substation for CORUS and Riverside substations. | 6/2000 | 10/2001 | 200000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 200000
700-6048 & 700-6047 | MW from Pleasanton to Charlotte substation. | Atascosa | MW equipment for Charlotte and Pleasanton substations. | 5/2000 | 6/2001 | 200000 |  |  | 30% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 200000
797-4074,797-4076, 897-4073 & 897-4075 | Digital MW from Vanderbilt to Danevang substation | Jackson | Digital MW equipment for Vanderbilt and Danevang substations. | 2/1997 | 6/2001 | 200000 |  |  | 30% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 200000
700-6022, 797-4072, 897-4071 & 800-6021 | Digital MW from Vanderbilt to El Toro substation | Jackson, Victoria | Digital MW equipment for Vanderbilt and El Toro substations. | 3/2000 | 6/2001 | 200000 |  |  | 30% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 200000
700-2071 & 800-2070 | Digital MW from Sam Rayburn substation to Goliad communication site. | Goliad, Victoria | Digital MW equipment for Sam Rayburn substation and Goliad communication site. | 6/2000 | 6/2001 | 200000 |  |  | 30% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 200000
700-6092 | MW Hop for Oaks 138 kV | Atascosa | MW Hop Equipment at Pleasanton substation for Oaks 138 kV substation. | 6/2000 | 10/2001 | 200000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 200000
799-4056, 799-4058, 899-4057 & 899-4055 | Digital MW from Bay City to Danevang substation | Matagorda | Digital MW equipment for Bay City and Danevang substations. | 6/1999 | 6/2001 | 200000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment arriving. |  | 200000
701.4019 &801.4018 | Lone Tree | Victoria | Upgrade to 10 MVA transformer. | 1/2001 | 6/2002 | 210000 |  |  | 25% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Equipment on order. |  | 210000
701.2022, 701.4020 &801.2021 | Van Vleck | Matagorda | Install 69 kV Arresters and add 5MVA transformer. | 1/2001 | 6/2001 | 225000 |  |  | 50% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Transformer received on site. |  | 225000
799-2080 | Edna Sub. add 69kV MODs | Jackson | Add 2 69 kV MODs at Edna substation & communications | 9/1999 | 5/2001 | 250000 |  |  | 90% | [7 empty] | CCN not required | Communication building installed |  | 250000
700-6054 &700-6055 | MW from Bay City to Van Vleck Substation | Matagorda | MW equipment for Bay City and Van Vleck and Tower | 5/2000 | 12/2000 | 300000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (i) | Closing out. |  | 300000
700-6058, 700-2057 & 700-6059 | Alice/San Diego Comm. Repeater | Duval, Jim Wells | MW Repeater Equipment & tower in Alice at Leona site. | 5/2000 | 6/2001 | 300000 |  |  | 30% | [7 empty] | 25.101 (c) (2) (C ) (i) | Equipment on order. |  | 300000
700-2083 & 800-2082 | San Diego | Duval | Install 69 kV breakers for Orange Grove and CPL line | 6/2000 | 6/2001 | 310000 |  |  | 8% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Planning only. |  | 310000
701-2029 | Ganado Tie | Jackson | Construct single circuit 69 kV line. | 6/2001 | 12/2001 | 320000 |  |  | 2% | 2 miles | #795 AAAC | Single pole. |  |  | 50 | 2 | pre-CCN | Ordered bid for fly over maps. |  | 320000
797-2175 | West Sinton Sw. | San Patricio | Install MW, SCADA & MOD | 10/1997 | 12/2000 | 330000 |  |  | 100% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Closing out. |  | 330000
New | Mathis | San Patricio | Install 2 69 kV Breakers and Comm. | 6/2001 | 6/2002 | 400000 |  |  | 1% | [7 empty] | CCN not required | Equipment on order. |  | 400000
700.9262 | Orange Grove 69 kV | Jim Wells | Exspand substation site for transformer and 69 kV additions. | 12/2000 | 6/2002 | 520000 |  |  | 10% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Equipment on order. |  | 520000
700.9401 | Pleasanton | Atascosa | Exspand substation site for transformer and 69 kV additions. | 12/2000 | 6/2002 | 520000 |  |  | 10% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Equipment on order. |  | 520000
798-4012,700-6007 & 898-4011 | Rebuild Ricardo substation to 5MVA | Kleburg | Build 5MVA steel frame substation and remove wood frame. | 7/1999 | 2/2001 | 550000 |  |  | 95% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Awaiting change over & removal of old station. |  | 550000
8992118 & 7992119 | Riverside Substation to Riverside Tap upgrade | Nueces | Rebuild 4/0 line to 795 kcmil line | 01/2001 | 2001-09-01 | 590000 |  |  | 8% | 4.46 | 795 kcmil | concrete tubular | 50 | 4.46 | existing |  | 25.101 (c) (2) (C ) (ii) | Upgrades necessary due to flow through during certain line outages |  | 590000
700-2005 | Double Arm portion of 69 kV system. | Atascosa | Double arming of a portion of the 69 kV system. | 1/2000 | 12/2003 | 608000 |  |  | 66% | [7 empty] | 25.101 (c) (2) (C ) (ii) | In Progress. |  | 608000
700.2361 | Mathis | San Patricio | Construct single circuit 69 kV line. | 6/2001 | 6/2002 | 680000 |  |  | 5% | 4.25 mi. | #795 AAAC | concrete tubular |  |  | 50 | 4.25 | pre-CCN | Received overhead maps. |  | 680000
799-2089, 899-2088, 899-1092 & 899-4090 | Port O'Connor | Calhoun | Exspand existing substation | 10/1999 | 10/2002 | 850000 |  |  | 8% | [7 empty] | 25.101 (c) (2) (C ) (ii) | Communications building installed. |  | 850000
799-2119 | Riverside and City of Robstown additions for CCN lines | Nueces | Substation additions to accommodate new lines | pre-CCN | 2001-09-01 | 885000 |  |  | 10% | [7 empty] | pre-CCN | CCN Filed 11/2000. Settlement with land owners completed. |  | 885000
700-2004 & 800-2003 | Install & remove poles in the 69 kV system. | system wide | Install new pole in the 69 kV system. | 1/2000 | 12/2003 | 945000 |  |  | 51% | [7 empty] | 25.101 (c) (2) (C ) (ii) | In Progress. |  | 945000
700-2080 | Calallen to Riverside Tap Double Circuit & City of Robstown to Riverside 69 kV single Ckt. | Nueces | 1) Rebuild single ckt line to dbl. ckt line; 2) build new line between City of Robstown and STEC's Riverside substation | pre-CCN | 2001-09-01 | 1211000 |  |  | 8% | 0.66 & 6.5 | 795 kcmil | concrete tubular | 50 | 0.66 | 50 | 6.5 | pre-CCN | CCN Filed 11/2000 |  | 1211000
7991095 | Rossville Dist. Substation | Atascosa | 138/12.5 kV dist. Subatstion | 4/2000 | 3/2001 | 2130000 |  |  | 25% | [7 empty] | 21498 | Transformer received on site. |  | 2130000
7992014 & 7002074 | San Miguel Sw. Sta. Additions | Atascosa | 345 kV additions | 11/2000 | 2002-07-01 | 2500000 |  |  | 34% | [7 empty] | 21747 | Material on order. |  | 2500000
none | Build new Jourdanton substation. | Atascosa | Build new 10 MVA 138/12 kV substation in near Jourdanton. | 10/2000 | 9/2001 | 2525000 |  |  | 3% | [7 empty] | 25.101 (c) (2) (B) | Site location on going |  | 2525000
7982061 | Oaks 138/69 kV additions | Atascosa | 138/69 kV Additions | 6/2000 | 5/2001 | 2550000 |  |  | 25% | [7 empty] | 21498 | Peers poured for foudation work. |  | 2550000
none | Build new Warburton (McFaddin) substation. | Victoria | Build new 138/69 kV substation on Warburton Road near McFaddin. | 10/2000 | 12/2001 | 2700000 |  |  | 5% | [7 empty] | 25.101 (c) (2) (B) | Site has been purchased. |  | 2700000
7991120, 799-4124 & 800-4275 | Calallen Sub Rebuild | Nueces | Rebuild 69 kV Sw. Sta. | 6/2000 | 6/2001 | 2950000 |  |  | 22% | [7 empty] | 25.101 (c) (2) (B) | Material in process of bids. |  | 2950000
7982060 | Oaks - Somerset 138 kv | Atascosa, Bexar | Single Ckt. 138 kV line | 2/2000 | 5/2001 | 4675000 |  |  | 50% | 18.2 | 795 kcmil | concrete tubular |  |  | 100 | 18.2 | 21498 | ROW acquired, 100% ROW clearing & 55% of poles set. |  | 4675000
7992014 & 7002075 | Pawnee Sw. Sta. | Karnes | New 345/138 kV Sw. Sta. | 11/2000 | 2002-07-01 | 10609400 |  |  | 34% | [7 empty] | 21747 | Material on order. |  | 10609400
7992014 & 7992006 | San Miguel-Pawnee 345 kV | Live Oak, Karnes, Atascosa | Construct Dbl Circuit 345 kV line w/ One circuit initially | 11/2000 | 2002-07-01 | 30000000 |  |  | 34% | 35 miles | 2-1590 kcmil per phase | Single pole. |  |  | 115 ft | 35 miles | 21747 | Survey & centerline 90%, property work in progress, poles designed and out for bids. |  | 30000000
700-2065 & 800-2064 | Salem Road | Victoria | Relocate 6 poles on Highway widening | 5/2000 | 12/2000 | Reimbursable |  |  | 100% |  |  |  | 50 | 1500 | 50 | 1500 | 25.101 (c) (2) (C ) (iii) | Closing out. |  | Reimbursable
0
0
0
0
0
0
0
[19 empty] | 0 | 81615400 | 81615400
CONSTRUCTION COSTS
CONSTRUCTION COSTS
CONSTRUCTION COSTS
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## SPEC
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | CONSTRUCTION COSTS |  | VAR.(%) | % COM | LENGTH | CONDUCTOR | STRUCTURE | RIGHT-OF-WAY |  |  |  | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
[13 empty] | EXISTING |  | NEW
[6 empty] | ESTIMATED | FINAL | [5 empty] | W | L | W | L
| Cooper 69 kV Transmission Tap | Lubbock County | Install New 69 kV line ( two spans) into new distribution substation | 2001-01-04 | 2001-07-04 | 855003 |  |  |  | 403 ft |  |  | 103 ft | 400ft
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
CONSTRUCTION COSTS
0
ESTIMATED
855003
[19 empty] | 0 | 855003 | 855003

## SPS
RIGHT-OF-WAY
PROJECT NUMBER. | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
401-5245 | 345 kV Amarillo, TX | Potter, Moore | Please See Docket No. 21460 | 2000-11-01 | 2001-09-01 | 34383108 | N/A | N/A | [8 empty] | Docket No. 21460 |  |  | 34383108
| to Holcomb, KS | Sherman, Hansford | Potter County to Harrington-Bushland | 2000-11-06 | 2001-09-01 | 783084 | N/A | N/A | 15% | 6,684 ft | 795 MCM ACSR | Two Pole Steel H-Frame | N/A | N/A | 80 ft | 6,684 ft
|  | Counties, Texas | Potter County to Oklahoma | 2000-11-19 | 2001-09-01 | 24117561 | N/A | N/A | 40% | 504,768 ft | 795 MCM ACSR | Two Pole Steel or Wood H-Frame | N/A | N/A | 150 ft | 504,768 ft
|  |  | Potter County Switching Station | 2000-11-01 | 2001-09-01 | 9482463 | N/A | N/A | 15% | N/A | N/A | N/A | N/A | N/A | N/A | N/A
0
401-5606 | Pullman Substation | Potter and Randall Counties | Please See Docket No. 22212 | 2000-06-01 | 2000-08-30 | 2157719 |  | N/A | [8 empty] | Docket No. 22212
|  |  | Southeast Sub to Pullman Sub | 2000-06-01 | 2000-08-30 | 960554 | 2084887 | 117.0505 | 100% | 22,176 ft | 397.5 MCM ACSR | Single-Shaft Steel or Concrete | N/A | N/A | 60 ft | 22,176 ft |  | See Attached Explanation | 960554
|  |  | Pullman Sub | 2000-06-01 | 2000-08-30 | 1197165 | 1261801 | 5.3991 | 100% | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  | 1197165
0
| Adobe Creek and CRMWA #22 |  | Please See Docket No. 23002 | 2000-10-01 | 2001-02-01 | 3372001 | N/A | N/A | [8 empty] | Docket No. 23002 |  |  | 3372001
401-5267 | Adobe Creek | Gray and Roberts | New 13.25 mile 69kV line and Substation | 2000-10-01 | 2001-02-01 | 2998609 | N/A | N/A | N/A | 69,960 ft | 397.5 MCM ACSR | Single-Shaft Steel or Concrete and Two Pole Wood | N/A | N/A | 60 ft | 69,960 ft |  |  |  | O
401-5607 | CRMWA #22 | Carson | New 0.42 mile 69kV Line and Substation | 2000-10-01 | 2001-02-01 | 373392 | N/A | N/A | N/A | 2,218 ft | 4/0 ACSR | Two Pole Wood H-Frame | N/A | N/A | 60 ft | 2,218 ft |  |  |  | O
0
0
0
0
0
0
0
0
[5 empty] | W | L | W | L
[19 empty] | 2157719 | 37755109 | 39912828
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## SWEPCO
RIGHT-OF-WAY
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | COM (%) | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS |  | ESTIMATED
21343151 | Eastex Sub - Harrison Road Transmission | Gregg & Harrison Counties, Texas | Build new 138kV line from new Eastex switching station to Harrison Road Substation | 2000-08-28 | 2001-01-19 | 3230000 |  |  | 98% | 9.86 mi | 1272 ACSR | Single Pole |  |  | 75-100 ft | 9.86 mi |  | Docket #21900; approved 3/1/00 |  | 3230000
21555161.1 | Pilgrim's Transmission Reroute | Camp County, TX | Relocate approximately 1100' of Pittsburg-Petty 138kV line to the west, near the Pilgrim's new freezer facility. | 2001-07-02 | 2001-08-24 | 50000 |  |  |  | .2 mi | 1272 ACSR | Single Pole Concrete |  |  | 100 ft | .2 mi | 25.101(c)(2)(C)(iii) |  |  | 50000
22032516 | Bann-SE Texarkana 138kV Line | Bowie County, TX | Rebuild existing 69kV Bann-Texarkana Plant transmission line to 138kV construction. Construct 138kV double circuit tap from this line to the new S.E. Texarkana 138/69kV substation. | 2001-09-03 | 2001-12-21 | 2400000 |  |  |  | 11.32 mi | 1272 ACSR | Single Pole | 50-100 ft | 11.32 |  |  | 25.101(c)(2)(C)(ii) |  |  | 2400000
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[5 empty] | W | L | W | L
[19 empty] | 0 | 5680000 | 5680000
NEW
EXISTING
NEW
EXISTING
CONSTRUCTION COSTS

## TXU
RIGHT-OF-WAY
PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | COM (%) | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS
0
98T61075 | IH 35 & SH 190 | Carrollton, TX | Relocate and raise structure 4/11 (A). Raise existing structure | 2001-03-20 | 2001-06-01 | 216755 |  |  |  | .35 mi | (6) 1033 MCM ACSR | Steel Lattice Towers | 100' | 1870' |  |  | 25.101(c)(2)(C)(v) | Date from 4/1/01 to 3/20/01. Proj reported on |  | 216755 | 1
RHP/SEI | Norwood-Carrollton 138KV | Dallas County | 4/9 (D) in same location. Add two new structures ( B ) and ( C ). | [14 empty] | 2/20/01 report. |  | 0
|  |  | Remove structure 4/10. | [14 empty] | TXDOT Project. |  | 0
0
98T61076 | IH 35 & SH 190 | Carrollton, TX | Relocate and raise structures T230 and T231. | 2001-03-20 | 2001-06-01 | 116501 |  |  |  | .32 mi | (3) 1033 MCM ACSR | Steel Lattice Towers | 125' | 1675' |  |  | 25.101(c)(2)(C)(v) | Date from 4/1/01 to 3/20/01. Proj reported on |  | 116501 | 1
RHP/SEI | North Lake-Northhaven 138KV | Dallas County | [8 empty] | (3) 795 MCM ACSR | [6 empty] | 2/20/01 report. TXDOT Project. |  | 0
0
98T61077 | IH 35 & SH 190, NW Carrollton- | Carrollton, TX | Relocate and raise structures T330 and T331. | 2001-03-20 | 2001-06-01 | 113361 |  |  |  | .34 mi | (3) 1033 MCM ACSR | Steel Lattice Towers | 125' | 1770' |  |  | 25.101(c)(2)(C)(v) | Date from 4/1/01 to 3/20/01. Proj reported on |  | 113361 | 1
RHP/SEI | Renner 138 kV Line | Dallas County | [8 empty] | (3) 927.2 MCM ACSR | [6 empty] | 2/20/01 report. TXDOT Project. |  | 0
0
99T61014 | SH 66, Rockwall County | City of Rowlett | Relocate and replace (1) steel lattice structure. | 2001-04-02 | 2001-06-01 | 98505 |  |  |  | .19 mi | (6) 795 MCM ACSR | Steel Lattice Tower | 85' | 950' |  | 8228 sq ft | 25.101(c)(2)(C)(v) |  |  | 98505 | 1
BW/SEI | 138 kV Line | Rockwall County | [13 empty] | Irr Shape |  |  |  | 0
0
99T61029 | Royse-Tricorner 345 kV Line- | Kaufman County | Relocate approximately 0.3 miles of existing double circuit 345 kV | 2000-10-01 | 2000-12-31 | 1500000 |  |  | 100% | 0.6 mi. | 2-795 kcmil ACSR | Double Circuit | 250' | 1750' | 250' | 2850' | 25.101(c)(2)(C)(iii) | Final costs accumulating. |  | 1500000 | 1
DRC | Relocation For Duke Energy- |  | line to allow for the construction of Duke Energy-Kaufman's | [8 empty] | Lattice Steel Tower | [5 empty] | Project delay from 11/22/99. |  | 0
| Kaufman |  | 550 MW generating plant. | [16 empty] | 0
0
99T64069 | Jewett-Big Brown 345 kV Line- | Leon County | Replace existing foundations damaged by severe corrosion and | 1999-11-22 | 2000-12-20 | 580000 |  |  | 100% | 30 mi | 2-795 kcmil ACSR | Double Circuit | N/A | N/A | N/A | N/A | 25.101(c)(2)(C)(ii) | Final costs accumulating. |  | 580000 | 1
DRC | Add Found. Capacity/Vibration | Freestone County | install new vibration control dampers on existing conductor and | [8 empty] | Lattice Steel Tower | [7 empty] | 0
| Control |  | shield wires. | [16 empty] | 0
0
99T64071 | Martin Lake-Mt. Enterprise Switch | Rush County | Utilizing a 1.3 mile section of the existing 345 kV double circuit | 2000-04-01 | 2000-11-01 | 781514 |  |  | 100% |  | 2-1590 kcmil ACSR | Lattice Steel | 160' | 1.3 miles | 160' | 2000' | 25.101(c)(2)(C)(i) | Final costs accumulating. |  | 781514 | 1
00T64033 | and Stryker Creek-Mt. Enterprise |  | lattice steel Martin Lake-Nacogdoches (Mr. Enterprise- | [16 empty] | 0
00T64034 | Switch 345 kV Lines: Construct |  | Nacogdoches section) Line with one 2-795 kcmil circuit presently | [16 empty] | 0
WB | loop line to Mt. Enterprise Switch |  | in place, construct two 2-1590 kcmil circuits to the new | [16 empty] | 0
| for connecting Tenaska Gateway |  | Mt. Enterprise 345 kV Switching Station (Tenaska Gateway). | [16 empty] | 0
| Merchant Power Plant to the | [18 empty] | 0
| transmission grid. | [18 empty] | 0
0
99T65122 | Parkdale SES - Greenville | City of Dallas | Rebuild 6.6 miles of 138 kV double-circuit tower line, with | 1999-10-25 | 2001-05-18 | 3495000 |  |  | 82% | 6.6 mi. | 1033.5 ACSR | Single Pole | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Finish date from 12/31/00 to 1/31/01, from |  | 3495000 | 1
DRC | Ave, 138 kV Line Rebuild |  | bundled 1033 ACSR on single self-supporting poles. | [8 empty] | Steel / Concrete | [5 empty] | 1/31/01 to 5/18/01. |  | 0
0
99T65124 | Blackwell - Kirkland Park | City of Dallas | Rebuild 1.8 miles of 138 kV double-circuit tower line, with | 1999-10-25 | 2001-04-23 | 1650000 |  |  | 81% | 1.8 mi. | 1033.5 ACSR | Single Pole | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Associated with Projects 99T65124 |  | 1650000 | 1
DRC | 138 kV Line Rebuild |  | bundled 1033 ACSR on single self-supporting poles. | [8 empty] | Steel / Concrete | [5 empty] | and 99T65125. Finish dte frm 5/15/00 to 12/31/00. |  | 0
[18 empty] | Finish dte from 12/31/00 to 4/1 & 4/1 to 4/23/01. |  | 0
[18 empty] | Unable to gain line clearances. |  | 0
0
99T65125 | Kirkland Park - Northaven | City of Dallas | Rebuild 3.1 miles of 138 kV double-circuit tower line, with bundled | 1999-10-25 | 2001-04-08 | 2365000 |  |  | 80% | 3.1 mi. | 1033.5 ACSR | Single Pole | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Associated with Projects 99T65122 |  | 2365000 | 1
DRC | 138 kV Line Rebuild |  | 1033 ACSR on single self-supporting poles. | [8 empty] | Steel / Concrete | [5 empty] | and 99T65125 |  | 0
0
99T65126 | Norwood - Denton Drive | City of Dallas | Rebuild 3.7 miles of 138 kV double-circuit tower line, with bundled | 1999-10-25 | 2001-03-18 | 2146000 |  |  | 92% | 3.7 mi. | 1033.5 ACSR | Single Pole | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) |  |  | 2146000 | 1
DRC | 138 kV Line Rebuild |  | 1033 ACSR on single self-supporting poles. | [8 empty] | Steel / Concrete | [7 empty] | 0
0
99T65148 | NW Carrollton-Carrollton Tarpley | Dallas, TX | Change out a guyed angle deadend structure, add a tangent | 2001-01-31 | 2001-03-15 | 92933 |  |  | 100% | N/A | 927.2 kcmil ACSR | Concrete Structures | N/A | N/A |  |  | 25.101(c)(2)(C)(i) | Final costs accumulating. |  | 92933 | 1
RP | Rd. 138 kV Line Upgrade | Dallas County | H-frame, raise a lattice tower and modify two (2) lattice | [16 empty] | 0
|  |  | towers from deadend to tangent structures. This work was | [16 empty] | 0
|  |  | originally deferred indefinitely due to the addition of the | [16 empty] | 0
|  |  | E. Carrollton Switching Station. | [16 empty] | 0
0
99T65150 | DeSoto Switch - Relocate | Glenn Heights, TX | Relocate 0.3 miles of the Trinidad -Liggett 138 kV line | 2000-10-20 | 2001-01-31 | 150000 |  |  | 100% | 0.3 mi | 1033.5 ACSR | Remove 3 wood | N/A | N/A |  |  | 25.101(c)(2)(C)(iii) | Final costs accumulating. |  | 150000 | 1
RP | Trinidad - Liggett 138 kV |  | Install 1033.5 ACSR to tie back into the existing | [8 empty] | structures, install | [7 empty] | 0
| Line to the Perimeter of the |  | bundled 336 ACSR circuit. | [8 empty] | 3 steel towers | [7 empty] | 0
| Switch Station Site | [18 empty] | 0
0
00T61002 | FM 1187 345 kV Line | City of Crowley | Relocate and raise (1) Type V Steel Tower. | 2001-04-02 | 2001-06-01 | 83409 |  |  |  | .40 mi | (3) 1590 MCM ACSR | Steel Lattice Tower | 150' | 2090' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 83409 | 1
BW/SEI |  | Tarrant County | [17 empty] | 0
0
00T61003 | Sandy Lake Road 69 kV Line | City of Coppell | Relocate (3) 69 kV wood poles. | 2000-11-07 | 2000-11-07 | 10623 |  |  | 100% | .13 mi | (3) 4/0 Copper | Single Pole Wood | 50' | 691' |  |  | 25.101(c)(2)(C)(v) | City of Coppell - Final costs accumulating. |  | 10623 | 1
BW/SEI |  | Dallas County | [17 empty] | 0
0
00T61004 | Greenville-Flynn:Relocate | North of Continental | Tower T-156 on the 138kV Greenville Flynn double | 2000-11-09 | 2000-12-30 | 312000 |  |  | 100% | .07 mi | 795 kcmil ACSR | Double Circuit Steel Pole | 70' | 367' | 70' | 363' | 25.101(c)(2)(C)(iii) | Final costs accumulating. |  | 312000 | 1
DC | Tower T-156 For Parking | Street and IH 35E | circuit transmission line is being relocated to permit | [16 empty] | 0
| Garage | City of Dallas | construction of a parking garage for the City of Dallas | [16 empty] | 0
|  |  | project "American Airlines Arena". | [16 empty] | 0
0
00T61009 | IH 635 & GBT (SH 161) | City of Irving | Replace (2) existing tubular steel pole with taller tubular steel | 2000-12-27 | 2001-05-02 | 638837 |  |  | 40% | .62 mi | (3) 1590 MCM ACSR | Steel Lattice Towers/ | 133' | 3285' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 638837 | 1
BW/SEI | Norwood Hackberry Junction | Dallas County | poles at the same location. Replace and relocate (1) existing | [8 empty] | Tubular Steel Poles | [7 empty] | 0
| 345 kV |  | tubular steel pole with a new taller tubular steel pole. | [16 empty] | 0
0
00T61010 | IH 635 & GBT (SH 161) | City of Irving | Replace (4) lattice towers with taller tubular steel poles in the | 2000-12-27 | 2001-05-02 | 445800 |  |  | 40% | .86 mi | (6) 1033.5 MCM ACSR | Steel Lattice Towers/ | 133' | 4540.7' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 445800 | 1
BW/SEI | North Lake-Morrison 138KV | Dallas County | same location. Replace and relocate (1) lattice tower with a | [8 empty] | Tubular Steel Poles | [7 empty] | 0
|  |  | taller tubular steel pole. Resag conductor between nearest | [16 empty] | 0
|  |  | deadend structures. | [16 empty] | 0
0
00T61013 | Chandler Creek, Round Rock | City of Round Rock | Relocate and replace (2) wood H-Frame structures with (2) | 2000-06-06 | 2000-06-08 | 28357 |  |  | 100% | .43 mi | (3) 795 MCM ACSR | Wood/Concrete | 120' | 2274' |  |  | 25.101(c)(2)(C)(iv) | Final costs accumulating. |  | 28357 | 1
BW/SEI | 138 kV Line | Williamson County | concrete H-Frame structures to make way for cutting of new | [8 empty] | H-Frame | [7 empty] | 0
|  |  | streets in the Chandler Creek Development. | [16 empty] | 0
0
00T61014 | Cartwright Road Relocate | City of Mesquite | Relocate and replace (1) wood H-Frame structure. | 2000-10-05 | 2000-10-06 | 24188 | 29201 | 21% | 100% | .16 mi | (6) 636 MCM ACSR | Wood H-Frame | 100' | 835' |  |  | 25.101(c)(2)(C)(v) | Material and Labor costs more than estimated. | 24188 |  | 1
BW/SEI |  | Dallas County | [15 empty] | City of Mesquite - Widening of Cartwright Rd. |  | 0
0
00T61015 | FM 1382 Relocate | City of DeSoto | Relocate and replace (1) wood H-Frame structure. | 2000-12-18 | 2000-12-19 | 14958 |  |  | 100% | .18 mi | (3) 1033 MCM ACSR | Wood H-Frame | 85' | 950' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project - Final costs accumulating. |  | 14958 | 1
BW/SEI |  | Dallas County | [17 empty] | 0
0
00T61017 | TXDOT I635&US75 Line | City of Dallas | Convert the Schroder Rd. Sub to TI Sub 138kV double | 2000-11-13 | 2001-05-15 | 6000000 |  |  | 35% | (1) - .48 mi | 3500 kcmil compact | 8" Fluid Filled Steel | 100' | 1785' |  |  | 25.101(c)(2)(C)(v) |  |  | 6000000 | 1
00T61018 | Relocations | Intersection of I635 & | circuit line section and the section of the Walnut St | [7 empty] | segmental copper | Pipe | [7 empty] | 0
WB |  | US 75 | 138kV single circuit tap to the Air Liquide Tap from an | [6 empty] | (2) - .76 mi | 138 kV HPFF cable | Concrete encased | [7 empty] | 0
|  |  | overhead transmission system to an underground | [7 empty] | 2000kcmil XLPE | PVC 3 X 3 duct | [7 empty] | 0
|  |  | system. Overhead facilities to be removed after | [7 empty] | copper underground | structure | [7 empty] | 0
|  |  | underground system in place. | [7 empty] | cable | [8 empty] | 0
0
00T61024 | Grande Boulevard | City of Tyler | 138 kV line consists of removing 4 (four) "H" frame structrures | 2001-04-01 | 2001-10-30 | 553872 |  |  |  | .62 mi | 1590 ACSR | Single Pole DC Structure | 150' | 1265' | 150' | 1265' | 25.101 (c)(2)(C)(v) | Interim Report Filed 3/1/01. |  | 553872 | 1
BM/WB | Pole Replacement | Smith County | and replace them with 5 (five) single pole concrete structures | [7 empty] | 1750 AAC | Single Pole SC Structure | 100' | 1986' | 100' | 1986' |  |  |  | 0
|  |  | 345 kV line consists of removing 1 (one) lattice tower structure | [16 empty] | 0
|  |  | and adding 2 (two) single pole steel structures. Construction | [16 empty] | 0
|  |  | on transmission lines is due to the extension of Grande | [16 empty] | 0
|  |  | Boulevard to Hwy 69. | [16 empty] | 0
0
00T61025 | SH 24, Commerce | North of the City of | Relocate and replace (3) wood H-Frame structures with (3) | 2001-03-20 | 2001-06-01 | 90458 |  |  |  | .42 mi | (3) 336.4 MCM ACSR | Wood / Concrete | 120' | 2225' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 90458 | 1
BW/SEI |  | Commerce in Hunt County | taller concrete H-Frames. Remove (1) wood H-Frame due to | [8 empty] | H-Frames | [7 empty] | 0
|  |  | adjustment in span lengths with relocated concrete H-Frames. | [16 empty] | 0
|  |  | A temporary wood H-Frame is to be installed clear of new | [16 empty] | 0
|  |  | roadway to permit continued construction. Concrete H-Frames | [16 empty] | 0
|  |  | to be installed later. | [16 empty] | 0
0
00T61026 | US 82, Kell Frwy, Wichita Falls | City of Wichita Falls | Remove guy stub pole and add new deadend guyed steel pole. | 2001-04-02 | 2001-06-01 | 98173 |  |  |  | .34 mi | (6) 1798 MCM ACAR | Tubular Steel Poles | 0 | 1770' |  |  | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 98173 | 1
BW/SEI | 138 kV Line | Wichita County | Raise 1 steel pole and relocate, raise 1 steel pole. | [16 empty] | 0
0
00T61030 | Bus 114L at DART RR 138 kV Line | City of Grapevine | Relocate (1) steel pole. | 2001-04-02 | 2001-06-01 | 78786 |  |  |  | .16 mi | (3) 1033 MCM ACSR | Tubular Steel Poles | 80' | 844' |  | 2914 sq ft | 25.101(c)(2)(C)(v) | TXDOT Project. |  | 78786 | 1
BW/SEI |  | Tarrant County | [13 empty] | Irregular |  |  |  | 0
[16 empty] | Shape |  |  |  | 0
00T62042 | Dublin - Stephenville | Stephenville, Texas | Reconductor 12 miles of existing line with 1033.5 ACSR. Raise | 2000-02-01 | 2000-12-30 | 910000 |  |  | 100% | 12 mi. | 1033.5 ACSR | Wood H-frame | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Final costs accumulating. |  | 910000 | 1
RP | 138 kV Line Upgrade |  | selected wood H-frames for required ground clearance requirements. | [16 empty] | 0
0
00T62052 | Everman SW-Mansfield 138 kV | Ft. Worth, Texas | Rebuild 138 kV wood H-frame line with concrete pole | 2000-09-01 | 2000-10-15 | 1415635 | 1656395 | 17% | 100% | 7.7 mi | 1590 ACSR | Single poles, H-frame | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Material and labor costs more than estimated. | 1415635 |  | 1
WB | Line Rebuild | Tarrant County | structures; Reconductor 336.4ACSR with 1590 ACSR | [8 empty] | and 3 pole concrete | [7 empty] | 0
0
00T62058 | Hwy 67 & Cheroke, Comanche | City of Comanche | Replace and relocate (6) 69 kV wood poles with concrete poles. | 2000-11-09 | 2000-11-16 | 93162 |  |  | 100% | .39 mi | (3) #1 Copper | Single Pole | 80' | 2060' |  |  | 25.101(c)(2)(C)(v) | TXDOT - Final costs accumulating. |  | 93162 | 1
WB/SEI | 69KV | Comanche County | Remove (1) wood pole. Design at 138 kV level. | [8 empty] | Wood/Concrete | [7 empty] | 0
0
00T62070 | Everman 345 kV Loop Line | 1.5 miles south of I-20 | Construct approx. 0.3 mile of 345 kV line from the existing | 2000-09-11 | 2001-04-30 | 1052354 |  |  | 62% | .07 mi | Single ckt. of bundled | Steel Lattice Towers/ |  |  | 48' | 380' | 25.101(c)(2)(C)(iii) | Interim Report filed 8/16/00. |  | 1052354 | 1
00T62071 |  | along Timberview Rd.; | DeCordova-Sherry 345 kV Line to provide a loop into Everman | [7 empty] | 1590 MCM ACSR | Tubular Steel Poles | [5 empty] | Added Project Number 00T62070. |  | 0
01T62018 |  | 1 mi. sw of the Loop820/ | Substation. In order to construct this loop line, two spans of the | [14 empty] | Projects 00T62070 and 00T62071 are |  | 0
MM/BJP |  | US 287/I-20 interchange. | adjacent Everman-Cedar Hill 345 kV line will need to be relocated. | [14 empty] | 100% complete. Cost estimate was |  | 0
[18 empty] | revised due to foundation cost being |  | 0
[18 empty] | more than expected. Also, material cost |  | 0
[18 empty] | more than estimated. |  | 0
00T62081 | Mineral Wells-Jacksboro 69 kV | City of Mineral Wells, Palo | Relocate approx. .5 miles of the Mineral Wells-Jacksboro 69 kV | 2000-10-16 | 2000-11-30 | 260000 |  |  | 100% | .5 mi | 4/0 MCM ACSR | Single Concrete Poles | 60'-100' | 2640' |  |  | 25.101(c)(2)(C)(iii) | Final costs accumulating. |  | 260000 | 1
WB/BJP | Line: Cantex Relocation+B203 | Pinto County | Line from struc. #1/5 thru struc. #1/17 on single ckt. concrete | [14 empty] | At request and expense of customer. |  | 0
|  |  | poles to accommodate a plant expansion by Cantex Inc. | [16 empty] | 0
0
00T62087 | Wolf Hollow - DeCordova- | Hood County, Texas | Modify the existing DeCordova-Comanche Peak double-circuit | 2001-03-23 | 2001-11-15 | 350000 |  |  |  | .15 mi | Bundled 1590.0 ACSR | Lattice Steel Tower | 240' | N/A | N/A | N/A | 25.101(c)(2)(C)(i) | Interim Report filed 2/23/01. |  | 350000 | 1
RP | Comanche Peak 345 kV Line |  | 345 kV Line, Benbrook-Comanche Pk. Circuit, to loop into and | [16 empty] | 0
| Modifications . Loop Benbrook- |  | out of proposed Wolf Hollow 345 kV Switch Station. This | [16 empty] | 0
| Comanche Pk 345 kV Circuit into |  | station is being constructed adjacent to the existing | [16 empty] | 0
| Wolf Hollow Sw. |  | transmission line right-of-way. Loop circuits will consist of | [16 empty] | 0
|  |  | one span each to station deadends. | [16 empty] | 0
0
00T63015 | Odessa EHV 345 kV Switch-Panda | Ector County | Construct two single circuit 2-795 kcmil ACSR | 2000-09-01 | 2000-11-30 | 250000 |  |  | 100% | .19 mi | 795 kcmil ACSR | Lattice Steel Towers |  |  | 160' | 1000' | 25.101(c)(2)(C)(i) | Final costs accumulating. |  | 250000 | 1
WB | Energy International Odessa |  | 345 kV lines between TXU's Odessa EHV | [14 empty] | Project number from 00T63105 to 00T63015. |  | 0
| Merchant Plant Switch |  | Switching Station and Panda Odessa Merchant | [16 empty] | 0
|  |  | Plant Switching Station to integrate the proposed | [16 empty] | 0
|  |  | transmission grid. | [16 empty] | 0
0
00T64035 | Belton-Ft. Hood 138 kv: Replace | Bell County | Relocate existing line sectionalizing switches to a common | 2000-10-02 | 2000-10-19 | 205154 | 174624 | -15% | 100% | N/A | 795 ACSR | Wood Poles-Existing | 100' | N/A |  |  | 25.101( c )(2)(C)(ii) | Labor cost less than estimated. | 205154 |  | 1
MM | Line Sectionalizing Switches |  | steel pole structure due to accessibility problems with the | [8 empty] | Steel Pole to be added | [7 empty] | 0
|  |  | existing switches. Existing switches are mounted on wood | [8 empty] | Concrete H-frame to be | [7 empty] | 0
|  |  | poles. One existing wooden H-frame will be replaced with a | [8 empty] | added. | [7 empty] | 0
|  |  | concrete pole H-frame in conjunction with this project. | [16 empty] | 0
|  |  | This project will be worked in conjunction with 00T64036. | [16 empty] | 0
0
00T64036 | Temple Switch-Lampasas 138 kV: | Bell County | Relocate existing line sectionalizing switches to a common | 2000-10-02 | 2000-10-19 | 108405 | 84715 | -22% | 100% | N/A | 795 ACSR and 336.4 | Wood Poles-Existing | 100' | N/A |  |  | 25.101( c )(2)(C)(ii) | Labor cost less than estimated. | 108405 |  | 1
MM | Replace Line Sectionalizing Switches |  | steel pole structure due to accessibility problems with the | [7 empty] | ACSR | Steel Pole to be added | [7 empty] | 0
|  |  | existing switches. Existing switches are mounted on wood | [8 empty] | Concrete H-frame to be | [7 empty] | 0
|  |  | poles. Two existing wooden H-frames will be replaced with | [8 empty] | added. | [7 empty] | 0
|  |  | concrete pole H-frames in conjunction with this project. | [16 empty] | 0
|  |  | This project will be worked in conjunction with 00T64035. | [16 empty] | 0
0
00T64046 | S. Temple-Belton 138 kV | City of Temple, TX | Reconductor the Temple Sw.-Lampases Co. 138 kV Trans- | 2000-10-20 | 2000-12-31 | 588258 |  |  | 100% | 5 mi | 795 kcmil ACSS "Drake" | Wood and Concrete | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Final costs accumulating. |  | 588258 | 1
RP | Reconductor |  | mission Line, from the South Temple Substation to the Belton | [8 empty] | H-frames. | [7 empty] | 0
|  |  | Substation. Replace and/or modify wood H-frame structures. | [16 empty] | 0
|  |  | Four wood H-frames will be replaced with concrete H-frames. | [16 empty] | 0
|  |  | All porcelain insulators will be replaced with polymer units. | [16 empty] | 0
0
00T64047 | N. Herty-E. Lufkin 138 kV | Lufkin, TX | Reconductor the 138 kV circuit from the North Herty Switch | 2002-01-02 | 2002-05-15 | 2033323 |  |  |  | 9.5 mi. | 1590 kcmil ACSR | Replace steel poles |  |  | N/A | N/A | 25.101(c)(2)(C)(ii) | Project has been deferred until 2002. |  | 2033323 | 1
RP | Reconductor Project |  | Station to the East Lufkin Substation with 1590 kcmil ACSR. | [8 empty] | hybrid poles; | [7 empty] | 0
|  |  | Replace steel poles with hybrid concrete/steel poles. H-Frame | [8 empty] | H-frames with | [7 empty] | 0
|  |  | portion will be rebuilt with single pole concrete construction. | [8 empty] | concrete poles. | [7 empty] | 0
|  |  | Steel lattice portion of the line will be analyzed for the addition | [16 empty] | 0
|  |  | of a second circuit. | [16 empty] | 0
0
00T64049 | Structure 36/7 Relocate | Anderson County | Relocate and replace (1) wood H-Frame structure that has | 2000-10-09 | 2000-10-10 | 29734 | 18307 | -38% | 100% | .23 mi | (3) 795 MCM ACSR | Wood H-Frame | 120' | 1190' |  |  | 25.101(c)(2)(C)(iv) | Material and labor costs less than estimated. | 29734 |  | 1
BW/SEI | 138KV |  | been encroached upon by a pond. Add (1) new wood H-Frame | [14 empty] | Water encroachment. |  | 0
|  |  | structure to reduce span length. | [16 empty] | 0
0
00T64050 | Structure 29/10 Relocate | Southwest of Palestine in | Relocate and replace (1) wood H-Frame structure that has | 2000-10-09 | 2000-10-10 | 8371 |  |  | 100% | .19 mi | (3) 795 MCM ACSR | Wood H-Frame | 120' | 1020' |  |  | 25.101(c)(2)(C)(iv) | Water encroachment. Final costs accumulating. |  | 8371 | 1
BW/SEI | 138KV | Leon County | been encroached upon by a pond. | [16 empty] | 0
0
00T65007 | Mayfield Rd. Substation: | Tarrant County | Add second circuit on existing steel poles to provide an | 2000-09-15 | 2000-11-02 | 1059107 |  |  | 100% | 2.9 mi. | 795 kcmil ACSR | Steel Poles | 100' | 2.9 |  |  | 25.101( c )(2)(C)(ii) | Final costs accumulating. |  | 1059107 | 1
MM |  |  | additional 138 kV feed from the south to Mayfield | [16 empty] | 0
|  |  | Road Sub. | [16 empty] | 0
0
00T65048 | Carrollton East 138 kV Switch | Dallas, TX | Line work to terminate the NW Carrollton-Renner and North | 2001-03-01 | 2001-03-30 | 531224 |  |  |  | 0 mi. | 795 kcmil ACSR | Add 2 lattice steel |  |  | N/A | N/A | 25.101(c)(2)(C)(ii) |  |  | 531224 | 1
RP | Station-Addison Taps 1 & 2 |  | Lake-Northaven 138 kV Transmission Lines into the new | [7 empty] | 927.2 kcmil ACAR | angle deadend | [7 empty] | 0
|  |  | switch station. Establish Addision Tap 1 to connect the | [7 empty] | 1033.5 kcmil ACSR | structures; 1 lattice steel | [7 empty] | 0
|  |  | existing west circuit of the Addison 138 kV Loop to the new | [8 empty] | tangent tower; replace | [7 empty] | 0
|  |  | Carrollton East-Carrollton Josey Lane 138 kV line section | [8 empty] | 1 lattice steel tangent | [7 empty] | 0
|  |  | & establish Addision Tap 2 to connect the existing east | [8 empty] | tower. | [7 empty] | 0
|  |  | circuit of the Addison 138 kV Loop to the new Carrollton East- | [16 empty] | 0
|  |  | Carrollton Tarpley Road 138 kV line section. Install line | [16 empty] | 0
|  |  | sectionalizing switches on the Addison Loop circuits at the new | [16 empty] | 0
|  |  | tap locations. | [16 empty] | 0
0
00T65087 | Mesquite Forney - Thornton | Mesquite, Texas | Reconductor 5 spans of 636 ACSR with 1590 ACSR conductor. | 2000-04-01 | 2001-05-01 | 130000 |  |  | 15% | 0.4 mi. | 1590 ACSR | Single Pole | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Work on project has been deferred. |  | 130000 | 1
DRC | East 138 kV Line Upgrade |  | Replace four wood H-frame structures with single concrete poles. | [8 empty] | Concrete | [5 empty] | Project delay from 2/1/00. |  | 0
0
00T65089 | Monticello SES-Farmersville | Collin, Delta, Franklin, | Construct new Farmersville Switching Station at the junction of | 2000-06-12 | 2000-12-07 | 20351457 |  |  | 100% | 81 mi | 1590 kcmil ACSR | Lattice Steel Towers | 170' | 81 mi. |  |  | 25.101(c)(2)(C)(ii) | Final costs accumulating. Conductor installation |  | 20351457 | 1
MM | Switching Station 345 kV Line, | Hunt, Titus Counties | Monticello SES-Valley Jct.-Royse 345 kV Line and the | [14 empty] | complete. Cost estimate increased due |  | 0
| Add Second Circuit |  | Valley-Royse 345 kV Line. Add a second 345 kV circuit to the | [14 empty] | to the necessity to install the new circuit |  | 0
|  |  | existing 81 miles of double circuit towers for ERCOT constraint | [14 empty] | with the adjacent circuit energized. Additionally, |  | 0
|  |  | project. | [14 empty] | wet conditions during construction caused |  | 0
[18 empty] | unexpected damage to the ROW. These factors |  | 0
[18 empty] | increased labor costs. |  | 0
0
00T65090 | Sulphur Springs Sw.- | Sulphur Springs | Reconductor 3.2 miles of existing line with 1590 ACSR (Falcon). | 2000-04-10 | 2000-12-30 | 895000 |  |  | 100% | 3.2 mi. | 1590 ACSR (Falcon) | Single Pole Concrete | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Final costs accumulating. |  | 895000 | 1
RP | Sulphur Springs 138 kV Line |  | Replace existing wood H-frames with single concrete poles. | [14 empty] | Finish date from 6/15/00 to 11/15/00. |  | 0
| Rebuild | [16 empty] | Unable to gain line clearances. |  | 0
[18 empty] | Interim Report filed 3/8/00. |  | 0
0
00T65100 | Liggett - Collin 138 kV Line: Loop | Dallas County | Install two spans of 795 kcmil conductor into Valley | 2000-08-01 | 2000-09-25 | 442000 | 455272 | 3% | 100% | 0.30 mi | 795 kcmil ACSR | Single pole structures |  |  | 75' | 0.30 mi | 25.101(c)(2)(C)(i) | Final costs accumulating. | 442000 |  | 1
WB/JS | into Valley Ranch Substation |  | Ranch Substation on double circuit steel poles. These | [14 empty] | Project delay. Lack of labor resources. |  | 0
|  |  | two spans will be constructed on TXU property. | [16 empty] | 0
0
00T65101 | Northlake - Morrison 138 kV Line: | Dallas County | Install two spans of 1033 kcmil conductor into Valley | 2000-08-01 | 2000-10-15 | 409000 | 360630 | -12% | 100% | 0.14 mi | 1033 kcmil ACSR | Single pole structures |  |  | 75' | 0.14 mi | 25.101(c)(2)(C)(i) | Labor costs less than estimated. | 409000 |  | 1
WB/JS | Loop into Valley Ranch |  | Ranch Substation on double circuit steel poles. These | [14 empty] | Interim Report filed 3/8/00. |  | 0
| Substation |  | two spans will be constructed on TXU property. | [14 empty] | Project delay. Lack of Labor resources. |  | 0
0
00T65102 | Norwood - Hackberrry 345 kV Line: | Dallas County | Reconfigure a section of an existing single circuit | 2000-08-01 | 2001-06-01 | 271000 |  |  | 50% | 0.54 mi | 1590 kcmil ACSR | Single pole structures | 150' | 2851' |  |  | 25.101(c)(2)(C)(ii) | Interim Report filed 3/8/00. |  | 271000 | 1
WB/JS | Modifications at Valley Ranch |  | 345 kV transmission line on steel poles to allow | [14 empty] | Project delay. Lack of labor resources |  | 0
| Substation |  | changes within Valley Ranch Substation. | [16 empty] | 0
0
00T65116 | Rivercrest-Clarksville 69 kv Line | Clarksville, Texas | Provide a 69 kv Point of Interconnection to Rayburn Country's | 2000-11-20 | 2001-03-31 | 75000 |  |  | 95% | .03 mi. | 336 kcmil ACSR | Concrete poles |  |  | 70' | 166' | 25.101(c)(2)(C)(i) | Lamar County Electric Coop will |  | 75000 | 1
RP |  |  | Lamar County Electric Coop. ,by installing a 69 kv Tap Switch | [14 empty] | provide the additional new right of way |  | 0
|  |  | Structure in TXU Electric & Gas Rivercrest-Clarksville 69 kv line | [14 empty] | required for this project. |  | 0
|  |  | and installing approximately a 140 foot slack span to the | [16 empty] | 0
|  |  | customer's deadend and structure and point of interconnection. | [16 empty] | 0
0
00T65117 | Commerce-Paris 69 kv line | Enloe, Texas | Provide a 69 kv Point of Interconnection to Rayburn Country's | 2000-11-27 | 2001-01-31 | 77000 |  |  | 100% | .03 mi. | 336 kcmil ACSR | Concrete poles |  |  | 70' | 140' | 25.101(c)(2)(C)(i) | Lamar County Electric Coop will |  | 77000 | 1
RP |  |  | Lamar County Electric Coop., by installing a 69 kv Tap Switch | [14 empty] | provide the additional new right of way |  | 0
|  |  | Structure in TXU Electric & Gas Commerce-Paris 69 kv line | [14 empty] | required for this project. |  | 0
|  |  | and installing approximately a 160 foot slack span to the | [14 empty] | Final costs accumulating. |  | 0
|  |  | customer's deadend and structure and point of interconnection. | [16 empty] | 0
0
00T65133 | St. Augustine Relocate | City of Dallas | Relocate (2) steel poles. | 2000-08-13 | 2000-10-06 | 61401 | 72485 | 18% | 100% | .23 mi | (3) 336 MCM ACSR | Tubular Steel Pole | 0 | 1225' |  |  | 25.101(c)(2)(C)(v) | City of Dallas - Intersection improvements. | 61401 |  | 1
BW/SEI | 138KV | Dallas County | [15 empty] | Material and labor costs more than estimated. |  | 0
0
00T65134 | Cooper-Paris 69 kV Arrester | Cooper, TX to Paris, TX | Upgrade to include replacing all porcelain insulators with | 2001-01-31 | 2001-04-20 | 417603 |  |  | 21% | 22 mi | 336.4 ACSR | Single Pole and | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) |  |  | 417603 | 1
RP | Installation Project |  | polymer units, installing lightening arresters on outside | [8 empty] | H-frame wood poles | [7 empty] | 0
|  |  | phases and install grounding systems for all tangent structures | [16 empty] | 0
|  |  | Change out four timber crossarms and six wood poles. | [16 empty] | 0
0
00T65135 | Line Work associated with Installing | Dallas, TX | Replace first tangent 345 kV steel pole south of the Liggett | 2000-10-20 | 2000-12-30 | 563518 |  |  | 100% | .2 mi | 1590 ACSR "Falcon" | 2-pole self-supportive | N/A | N/A |  |  | 25.101(c)(2)(C)(ii) | Final costs accumulating. |  | 563518 | 1
RP | 2nd Liggett 345/138 kV Auto- |  | Sw. Station with a 2-pole self-supporting angle dead end steel | [8 empty] | angel deadend steel | [7 empty] | 0
| transformer |  | structure. Conductor work will involve transferring the | [8 empty] | structure | [7 empty] | 0
|  |  | Venus-Liggett and Norwood-Liggett 345 kV circuits to the | [16 empty] | 0
|  |  | new structure to allow the addition of a second 345/138 kV | [16 empty] | 0
|  |  | autotransformer inside the Liggett Sw. Station | [16 empty] | 0
0
01T65074 | Farmersville-Valley Jct. 345 kV | Collin County | Add circuit to existing towers. This is part of the new circuit | 2001-03-26 | 2001-08-31 | 2452396 |  |  |  | 5.8 mi. | 1590 MCM ACSR | Lattice Towers | 170' | 30624' |  |  | 25.101(c)(2)(C)(ii) |  |  | 2452396 | 1
MM | Add circuit to existing towers |  | between Farmersville Sw. Sta. And Anna Sw. Sta. | [16 empty] | 0
0
01T65085 | Collin-Allen 138 kv Line: Line | City of Frisco, TX | Remove existing wood H-Frame struc. and install a 2-pole wood | 2001-03-20 | 2001-04-30 | 30600 |  |  |  | .21 mi | 795 MCM ACSR | Wood 2-Pole Guyed | 100' | 1100' |  |  | 25.101(c)(2)(C)(iii) |  |  | 30600 | 1
MM/BJP | modifications for construction | Collin County | small angle struc. to accommodate wire termination at new | [8 empty] | Small Angle Struc, | [7 empty] | 0
| of White Oak Sub |  | White Oak Substation Dead-End | [16 empty] | 0
0
01T65086 | Calumet - West Dallas 138 kV Line | City of Dallas | Raise two steel poles and one steel stub pole to provide | 2001-03-25 | 2001-04-15 | 94000 |  |  |  | N/A | 795 MCM ACSR | Single Circuit Steel Pole | 80' | 0 |  |  | 25.101(c)(2)(C)(iv) |  |  | 94000 | 1
ALK |  | County of Dallas | clearance over roadway | [16 empty] | 0
0
| CCN APPLICATIONS - APPROVED | [18 empty] | 0
97T62022 | Roanoke-Elizabeth Creek 138 kV | Denton County | Construct approx. 3 mi of 138 kV line and a new substation to |  |  | 3167000 |  |  |  | 3 mi | 1590 kcmil ACSR | Concrete and/or steel |  |  | 100' | 15840' | Docket No. 17686 | Project on hold for customer. |  | 3167000 | 1
BD | Line |  | provide service to Intel Corp new wafer fabrication facility. | [7 empty] | (each circuit) | pole structures | [7 empty] | 0
0
98T65088 | Limestone-Watermill 345 kV Line | Dallas, Ellis, Navarro, | Construct approximately 84 miles of 345 kV | 1999-11-15 | 2001-05-15 | 64361000 |  |  | 70% | ~84 mi | Twin-Bundle | Double Circuit Lattice |  |  | 160' | ~84 miles | Docket No. 21497 | Start date changed from 11/4/99. |  | 64361000 | 1
DRC |  | Freestone, Limestone | transmission line from the existing Reliant | [8 empty] | Steel Tower | [5 empty] | PCR filed 9/30/99 as Docket No. |  | 0
|  | Counties | HL&P Limestone SES to the existing | [14 empty] | 20790, prior to severed Docket No. |  | 0
|  |  | TXU Electric Watermill Switching Station. | [14 empty] | assignment. |  | 0
|  |  | This project has been designated a critical | [16 empty] | 0
|  |  | constraint relief project by the ERCOT ISO. | [16 empty] | 0
0
98T65088 | Limestone-Watermill 345 kV Line | Dallas, Ellis, Navarro, | Construct approximately 4 miles of 345 kV | 2000-03-01 | 2001-05-15 | 3239000 |  |  | 35% | ~4 mi | 1590 kcmil ACSR | Double Circuit Lattice |  |  | 160' | ~4 miles | Docket No. 20790 | PCR filed 11/20/99. |  | 3239000 | 1
DRC |  | Freestone, Limestone | transmission line from the existing Reliant | [7 empty] | Twin-Bundle | Steel Tower | [5 empty] | Final Order Open Meeting 1/27/00. |  | 0
|  | Counties | HL&P Limestone SES to the existing | [16 empty] | 0
|  |  | TXU Electric Watermill Switching Station. | [16 empty] | 0
|  |  | This project has been designated a critical | [16 empty] | 0
|  |  | constraint relief project by the ERCOT ISO. | [16 empty] | 0
0
99T64038 | Pflugerville South 138 kV | City of Pflugerville | Construct a double-circuit, 138 kV Transmission | 2001-03-12 | 2001-05-15 | 2163200 |  |  | 5% | 4.8 mi | 795 kcmil ACSR | Double circuit pole. |  |  | 40'-70' | 25344' | Docket No. 21777 | Application filed 12/6/99. Final order 10/20/00. |  | 2163200 | 1
MM | Transmission Line | Travis County | Line between the existing Pflugerville Substation | [8 empty] | (Steel or concrete will be | [5 empty] | PCR 12/20/00. Start date from 2/12/01 to 3/12/01. |  | 0
|  |  | and the proposed Pflugerville South Switching | [8 empty] | determined by bid.) | [5 empty] | Moved from CCNs pending to CCNs approved. |  | 0
|  |  | Station, needed to maintain reliable service to | [16 empty] | 0
|  |  | growing load in the Pflugerville-Round Rock- | [16 empty] | 0
|  |  | Georgetown area. | [16 empty] | 0
0
99T64040 | Round Rock Southeast 138 kV | Cities of Round Rock, | Construct a double-circuit, 138 kV Transmission | 2001-03-12 | 2001-05-15 | 8899700 |  |  | 5% | 4.9 mi | 795 kcmil ACSR | Double circuit pole. |  |  | 30'-50' | 25872' | Docket No. 21540 | Application filed 10/21/99. Final order 8/24/00. |  | 8899700 | 1
MM | Transmission Line | Pflugerville, Travis County, | Line between the existing Pflugerville 138 kV | [8 empty] | (Steel or concrete will be | [5 empty] | PCR 9/20/00. Start date from 1/17/01 to 3/12/01. |  | 0
|  | Williamson County | Transmission Line and the proposed Round Rock | [8 empty] | determined by bid.) | [7 empty] | 0
|  |  | Southeast Substation, needed to reliably serve | [16 empty] | 0
|  |  | the increasing load in the Round Rock/Pflugerville | [16 empty] | 0
|  |  | area. | [16 empty] | 0
0
99T65054 | Farmersville Junction-Anna | Collin County | Construct single circuit 345 kV line on double circuit towers | 2001-10-01 | 2002-12-15 | 13062600 |  |  |  | 19.4 mi | 1590 kcmil ACSR | Lattice steel towers | 150' | 3.32 mi | 160' | 16.08 mi | Docket No. 22665 | Application filed 6/13/00. Final order 11/1/00. |  | 13062600 | 1
MM | Switching Station Section of |  | between Farmesville Junction and the existing Anna Switching | [14 empty] | PCR 1/20/01. Start date from 2/20/01 to 10/1/01. |  | 0
| the Monticello-Farmersville |  | Station. This is an ISO constraint project. | [16 empty] | 0
| Switching Station-Anna | [18 empty] | 0
| Switching Station 345 kV Line | [18 empty] | 0
0
| CCN APPLICATIONS - PENDING | [18 empty] | 0
98T65024 | Plano Tennyson 138 kV Loop Line | Cities of Plano, The Colony, | Construct approximately 5.46 miles of 138 kV | 2000-09-01 | 2000-12-31 | 8967000 |  |  |  | 5.46 mi | 1590 kcmil ACSR | Double circuit pole | 70' | 28829' | 30' | 300' | Docket No. 21664 | Application filed 11/16/99. All information |  | 8967000 | 1
BD |  | and Carrollton, Counties of | transmission line from the existing N.W. Carrollton- | [8 empty] | (Steel or concrete to be | [5 empty] | estimated pending certificate approvel. Notice |  | 0
|  | Collin and Denton | Collin SES 138 kV Line to the existing Plano | [8 empty] | determined by bid.) | [5 empty] | provided. A small triangle of ROW will be |  | 0
|  |  | Tennyson Switching Station. | [14 empty] | required (30'X300') |  | 0
0
99T62045 | Morgan Creek-Twin Buttes-Red | Mitchell, Brown, Comanche | Construct approximately 70.6 miles of single circuit 345 kV | 2001-06-06 | 2002-12-31 | 37144000 |  |  |  | 70.6 | 1590 kcmil ACSR twin- | Double Circuit Lattice |  |  | 160' | 70.6 miles | Docket No. 22823 | Application filed 7/24/00. All information |  | 37144000 | 1
BD | Creek-Comanche 345 kV Line | Counties | transmission line on double circuit lattice steel towers. | [7 empty] | bundled conductor | Steel Towers | [5 empty] | estimated pending certificate approval. |  | 0
|  |  | This is a 215.1 mile ISO Critical Constraint Relief Project | [14 empty] | Notice provided. Intervention deadline |  | 0
|  |  | being certificated individually and constructed jointly with WTU. | [14 empty] | 9-7-00. |  | 0
0
99T65115 | Liggett-Euless-Hackberry 138 kV | City of Irving | Construct 3.2 miles of double circuit 138 kV transmission | 2001-02-19 | 2001-05-15 | 3689900 |  |  |  | 3.2 mi | 1033 kcmil ACSR twin- | Double Circuit (Steel | 40'-70' |  |  |  | Docket No. 23352 | Application filed 12/1/00. All information |  | 3689900 | 1
BD | Transmission Line | Dallas County | line on double circuit steel or concrete pole structues parallel | [7 empty] | bundled | or concrete poles to be | [5 empty] | estimated pending certificate approval. Notice |  | 0
|  |  | to the existing 138 kV line running north out of the Liggett Sw Station. | [8 empty] | determined by bid.) | [5 empty] | provided, Intervention deadline 1/15/01. |  | 0
0
99T65146 | Cedar Hill-DeSoto 138 kV 2nd Circuit | Cities of DeSoto, Glenn | Remove existing single-circuit 138 kV line on wood H-frames and | 2002-03-15 | 2002-05-15 | 4532000 |  |  |  | 6.2 mi | 1590 kcmil ACSR | Double Circuit (Steel | 75' | 32736' |  |  | Docket No. 23604 | Application filed 1/25/01. |  | 4532000 | 1
WB |  | Heights, Cedar Hill | replace with new double circuit 138 kV line on steel or concrete | [8 empty] | or concrete poles to be | [7 empty] | 0 | 65
|  | Dallas County | poles. | [8 empty] | determined by bid.) | [7 empty] | 0
0
COMPLETED PROJECTS REMOVED FROM 2/20/01 REPORT. | [19 empty] | 0
0
00J43506 | Wortham Coolidge Tap: upgrade 11mi | Limestone | Upgrade of 11 miles of 69 kV line. Installed lightning arrestors | 2000-06-01 | 2000-09-01 | 275000 | 350000 | 27% | 100% | 11 mi | 4/0 ACSR & 1/0 SOLID | Single Wood Poles |  | 11 mi | N/A | N/A | 25.101 (c)(2)(C)(v) | Actual costs for material and labor more than
BM/WB | of 69 kV line |  | to top phase of line. | [7 empty] | Copper 50% each | [6 empty] | estimated. |  | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 2695517 | 203379615 | 206075132
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## WTU
RIGHT-OF-WAY
PROJECT NUMBER. | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS |  | ESTIMATED
20317746 20075227 20127371 | Big Lake to Sonora | Crokett, Reagan & Sutton Counties | Build 73.3 miles of 138 kv line. The line is needed to relieve 69 kv systems overloads which occur during certain contingencies and to provide voltage support to the city of Ozona. | (8/23/99) | (5/6/00) | 12042300 | 8777856 | 72.89% | 99% | 73.3 | 477 KCM ACSR 26/7 ACSR | Single Pole |  |  | 70 | 73.3 |  | Full CCN, Docket #19670, Line construction complete 5/6/00, waiting for charges to clear to complete report. |  | 12042300
20970831 21977610 22678594 | Morgan Creek-Twin Buttes-Red Creek-Commanche 345 kV | Coke, Tom Green, Concho, McCulloch, and Coleman Counties | Build 144.7 Miles of 345 kV double circuit transmission lines on lattice towers | 2001-07-01 | 2003-06-01 | 83480444 |  |  | 0% | 289.44 | Bundled 1590 MCM | Double Circuit Lattice Towers |  |  | 160 ft. | 139.2 Mi. |  | Full CCN, Docket 22798 |  | 83480444
Removed: | [19 empty] | 0
0
Remarks: | Hearing on merits held 2/26/01 - 2/28/01 | [18 empty] | 0
0
Variance Explanation: | Big Lake to Ozona-The actual mileage was less than was originally estimated and the construction labor was 20-30% less than estimated. | [18 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 95522744 | 95522744
NEW
EXISTING
CONSTRUCTION COSTS