## SUMMARY
Revised: | 2005-08-01
MONTHLY ACTIVITY AT A GLANCE
for
FEBRUARY 2005
TRANSMISSION PROJECTS
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O
UTILITY | TOTAL PROJECTS REPORTED =Utility!AA102 | ESTIMATED COST FOR ALL REPORTED PROJECTS =Utility!AA100 | NEW PROJECTS COUNT THIS MONTH Manual Entry | 1st ESTIMATE COST FOR NEW PROJECTS Manual Entry | COMPLETED PROJECTS COUNT THIS MONTH =Utility!Y102 | COMPLETED PROJECTS (FINAL ACTUAL COSTS) =Utility!X100 | COMPLETED PROJECTS (FINAL ESTIMATED COSTS) =Utility!Y100 | ONGOING PROJECT COUNT = B - F | ONGOING PROJECT COST ESTIMATE (THIS MONTH) = C - H | ONGOING PROJECT COST ESTIMATE (FROM LAST MONTH) Linked or Manual | NET ONGOING PROJECT CHANGE FROM LAST MONTH = J - K | DIFFERENCE: NEW PROJECTS LESS COMPLETED PROJECTS = E - H | CALCULATED COST ADJUSTMENT TO EXISTING PROJECTS = L - M | EXPLANATION OR COMMENT
AEPC | 22 | 111011672 | 1 | 1245500 | 0 | 0 | 0 | 22 | 111011672 | 109766172 | 1245500 | 1245500 | 0
AEPN | 28 | 80152011 | 0 | 0 | 0 | 0 | 0 | 28 | 80152011 | 80152011 | 0 | 0 | 0
BEPC | 22 | 122983125 | 1 | 2913000 | 0 | 0 | 0 | 22 | 122983125 | 120070125 | 2913000 | 2913000 | 0
CNP | 27 | 90552000 | 5 | 6871000 | 3 | 7268545 | 8334000 | 24 | 82218000 | 83476000 | -1258000 | -1463000 | 205000 | Cost Revision 1 Project
EGSI | 26 | 73126337 | 7 | 6906132 | 1 | 326985 | 401888 | 25 | 72724449 | 66220205 | 6504244 | 6504244 | 0
EPE | 4 | 9514392.61 | 0 | 0 | 0 | 0 | 0 | 4 | 9514392.61 | 9514392.61 | 0 | 0 | 0
LCRA | 39 | 139047684.4879 | 8 | 3471000 | 1 | 7198241 | 8674000 | 38 | 130373684.4879 | 135576684.4879 | -5203000 | -5203000 | 0
MVEC | 5 | 8460000 | 0 | 0 | 0 | 0 | 0 | 5 | 8460000 | 8460000 | 0 | 0 | 0
LEA E.C. | [9 empty] | 0
PEC | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
SPS | 3 | 9920087 | 0 | 0 | 0 | 0 | 0 | 3 | 9920087 | 9920087 | 0 | 0 | 0
STEC | 18 | 4987000 | 0 | 0 | 0 | 0 | 0 | 18 | 4987000 | 4987000 | 0 | 0 | 0
SULP | 1 | 3978000 | 0 | 0 | 0 | 0 | 0 | 1 | 3978000 | 3978000 | 0 | 0 | 0
SWEPCO | 3 | 17639000 | 0 | 0 | 0 | 0 | 0 | 3 | 17639000 | 17639000 | 0 | 0 | 0
TNMP | 6 | 21700000 | 0 | 0 | 1 | 301000 | 100000 | 5 | 21600000 | 21700000 | -100000 | -100000 | 0
TXU | 98 | 340076694.04 | 14 | 32886605.04 | 1 | 6538590 | 44680 | 97 | 340032014.04 | 306112206.38 | 33919807.66 | 32841925.04 | 1077882.62 | Cost Revision 5 Projects
[15 empty] | Less: | 1077882.62 | (From Calc Cost Adj)
[15 empty] | = | -1077882.62 | (Difference)
TOTAL | 303 | 1033148003.1379 | 36 | 54293237.04 | 7 | 21633361 | 17554568 | 296 | 1015593435.1379 | 977571883.4779 | 38021551.66 | 36738669.04 | 1282882.62
|  | Ongoing Project Count Check: | 296 | Correct |  |  | LAST MONTH ONGOING COUNT: | 267
Note on A11: aboling: FORMERLY CPL.
Note on A12: aboling: FORMERLY WTU
Note on A14: aboling: FORMERLY CPE.
Note on A23: aboling: SHARYLAND UTILITIES
Note on A26: aboling: "Oncor" changed to TXU Electric Delivery Company.
Note on F10: aboling: A COMPLETE PROJECT IS DEFINED AS ONE FOR WHICH THE CONSTRUCTION IS COMPLETE AND THE FINAL ACTUAL PROJECT COST HAS BEEN ENTERED.
Note on I10: aboling: ACTIVE PROJECTS INCLUDE NEW PROJECTS BUT NOT COMPLETED PROJECTS.

## AEPC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
21071518 | Coleto Creek-Pawnee 345 kV | Goliad & Karnes Counties | New 345 kV line between Coleto Creek Power Station and new STEC Pawnee Switching Station | 2001-08-25 | 2003-09-30 | 2003-01-07 | 37887000 |  |  |  | 99% |  | 345kV | 107.8mi | Double Crkt 1590 MCM bundled | Steel Lattice Towers |  |  | 160 ft | 53.9 mi |  | Docket #21741 Final Order 6/18/01. Delay due to rain and US Fish & Wildlife restrictions. | 37887000 | 0 | 37887000 |  |  | 37887000 | 0 | 0
21722984 | Citgo NOP-Lon Hill 138 kV | Corpus Christi, Nueces County | Construct a new 138 kV transmission line from Citgo NOP to Lon Hill Sub in three secgments, 1.6 miles of single circuit single pole, 2.8 miles of double circuit single pole and 10. Miles of single circuit single pole. | 2002-04-18 | 2002-12-31 | 2003-01-14 | Transmission $9,369,033 Substation $4,663,624 |  |  |  | 99% |  | 138kV | 14.7 | 2-795 kcmil ACSR |  |  |  | 60' | 11.9 Mi |  | Docket #22338 Approved. STM approved to transfer 138kV transmission line only to LCRA in Docket #25774. Estimated cost of Transmission line to LCRA $9,667,731. Transmission portion listed in initial estimate includes ROW, which was not transferred to LCRA in the amount of $525,245. PUC Staff: LCRA July 2003 report shows this project 100% complete. Formula deleted to reflect that report. Projects remain only for informational purposes. |  | 0 | 0 | 4663624 |  | 0 | 0 | 0
21722970 | Citgo NOP-Nueces Bay 138 kV cable | Corpus Christi, Nueces County | Install 0.6 miles of underground cable from Citgo NOP substation to Nueces Bay Substation in conduit, 138 kV, 2-1000 kcmil Cu per phase in 4 conduits. | 2002-08-01 | 2002-02-01 | 2002-02-01 | Transmission $1,510,500 Substation $8,700,034 |  |  |  | 99% |  | 138kV | 0.6 Mi | 2-1000 kcmil Cu per phase in 4 Conduits | Cable |  |  | 20 | 0.6 Mi |  | Docket #22340 Approved. STM approved to transfer 138kV cable to LCRA in Docket #25774. Estimated cost of cable to LCRA $5,377,489. Transmission portion listed in initial estimate column includes ROW, which was not transferred to LCRA in the amount of $13,000. PUC Staff: LCRA July 2003 report shows this project 100% complete. Formula deleted to reflect that report. Projects remain only for informational purposes. |  | 0 | 0 | 8700034 |  | 0 | 0 | 0
21723002 | Lon Hill Power Station to Nueces Bay Power Station | Corpus Christi, Nueces County | Install a new 138 kV line in four segments from Lon C Hill Power Plant to Nueces Bay Power Plant. Segment 1-5.4 miles of double circuit single pole, Segment 2-0.2 miles of single circuit single pole, Segment 3-3.2 Miles of single circuit single pole, Segment 4-8.4 miles of double-circuit single pole, all constructed with 2-795 kcmil ACSR. | 2002-05-15 | 2002-05-15 | 2003-06-20 | Transmission $13,815,827 Substation $5,237,415 |  |  |  | 99% |  | 138kV | 17.2 | 2-795 kcmil ACSR | Single Pole With Davit Arm |  |  | 60' and 100' | 8.8 Mi |  | Docket #22339, CCN Approved. STM approved to transfer 138kV transmission line only to LCRA approved in Docket #25774. Estimated cost of transmission line to LCRA $26,300,779. Transmission portion listed in initial estimate column includes ROW, which was not transferred to LCRA in the amount of $13,000. FROM LCRA AUG RPT: Project substantially completed as of July 31, 2003. Remaining work to be completed by years end includes: oyster bay survey and othe items, such as installing a safety climbing device--projected costs for this work included in the final cost.Transferred from AEP Docket 25774, explanation of cost variance includes $8 million increase for bay crossing enginering, geotechnical and structures, $2.2 million in additional environmental protections and surveying costs, $0.7 million in construction change orders due to daily outage requirements and other issues, $0.2 million in pipeline adjustments. |  |  |  | 5237415 |  | 0 | 0 | 0
22169662 | Falcon-Lopeno 138 kV Line Reconductor | Starr & Zapata Counties, Texas | Reconductor and rebuild approximately 10 miles of existing 138kV transmission line from Falcon Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2001-12-15 | 2002-02-15 | 2002-02-21 | 2140875 |  |  |  | 95% | 138kV | 138kV | 10 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 10 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified service area. | 2140875 | 0 | 2140875 | 5237415 |  | 2140875 | 0 | 0
22169585 | Garza- Falcon 138 kV Line Reconductor | Starr County, Texas | Reconductor and rebuild approximately 27.3 miles of existing 138kV transmission line from Garza Substation to Falcon Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conductor on steel poles. | 2002-03-10 | 2002-10-10 | 2002-10-10 | 5577000 |  |  |  | 95% | 138kV | 138kV | 27.3 mi. | 795 MCM & 7#8 Alumoweld Static | Steel Single Poles | Ceterline Defined | 27.3 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | This line is located in MEC (Medina Electric Coop) single certified service area. | 5577000 | 0 | 5577000 |  |  | 5577000 | 0 | 0
22169764 | Lopeno-Zapata 138 kV Line Reconductor | Zapata County, Texas | Reconductor and rebuild approximately 20.3 miles of existing 138kV transmission line from Zapata Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-02-22 | 2003-01-30 | 2003-02-01 | 4168000 |  |  |  | 99% | 138kV | 138kV | 20.3 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 20.3 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified service area. | 4168000 | 0 | 4168000 |  |  | 4168000 | 0 | 0
22169796 | Rio Bravo-Zapata 138 kV Line Reconductor | Zapata & Webb Counties, Texas | Reconductor and rebuild approximately 30.8 miles of existing 138kV transmission line from Zapata Substation to Rio Bravo Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-05-15 | 2003-04-15 | 2003-05-15 | 6308000 |  |  |  | 99% | 138kV | 138kV | 30.8 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 30.8 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified & TCC single certified service areas. | 6308000 | 0 | 6308000 |  |  | 6308000 | 0 | 0
22169830 | Wormser-Rio Bravo 138kV Reconductor | Webb County, Texas | Reconductor and rebuild approximately 9.6 miles of existing 138kV transmission line from Rio Bravo Substation to Wormser Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-06-15 | 2003-05-15 | 2003-11-19 | 2201000 |  |  |  | 99% | 138kV | 138kV | 9.6 mi. | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Center line Defined | 29.6 mi. |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified & TCC single certified service areas. | 2201000 | 0 | 2201000 |  |  | 2201000 | 0 | 0
24853426 | 138kV Nueces Bay / Whitepoint West (Dupont Ingleside) | Corpus Christi, Nueces County | Relocate one mile of line nearest Nueces Bay Sub | 2002-09-30 | 2003-04-02 | 2003-03-01 | 355000 |  |  |  | 90% |  |  | 1 mi | 795 MOM ACSR | Tubular Steel |  |  |  |  | SUB R. 25.101(c)(2)(C)(iv) | Permit extending from Docket No. 22339 | 355000 | 0 | 355000 |  |  | 355000 | 0 | 0
24853427 | 138kV Nueces Bay / Whitepoint East (Portland) | Corpus Christi, Nueces County | Relocate .5 mile of line nearest Nueces Bay | 2002-09-30 | 2003-04-02 | 2003-03-01 | 240000 |  |  |  | 90% |  |  | .5 mi | 795 MOM ACSR | Tubular Steel |  |  |  |  | SUB R. 25.101(c)(2)(C)(iv) | Permit extending from Docket No. 22339 | 240000 | 0 | 240000 |  |  | 240000 | 0 | 0
40097398 | Los Fresnos to Brownsville | Cameron County, TX | Relocate approximately 600' of the Los Fresnos to Brownsville 69 kV line for a new subdivision of the City of Brownsville | 2003-01-02 | 2003-01-31 | PUC STAFF: THIS PROJECT WAS CLOSED IN DECEMBER 2004. | [15 empty] | PUC STAFF: THIS PROJECT WAS CLOSED IN DECEMBER 2004. | 0 | 0 | 0 |  |  | 0 | 0 | 0
40015548 | Hidalgo - Southeast Edinburg 6.3 mile 138kv transmission line reconductor | Hidalgo County, Texas | Reconductor the approximately 6.3 miles of existing 138kv from Hidalgo to Southeast Edinburg. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Poles will remain the same. | 2003-02-10 | 2003-12-12 |  | 1446315 |  |  |  | 97% | 138kV | 138kV | 6.3 miles | Drake 795 MCM ACSS | Wood Single Poles | Centerline Defined | 6.3 miles |  |  | Sub Rule 25.101 (c) (5) (B) | The line is located in TCC single certified and in TCC / MVEC (Magic Valley) dual certified areas. | 1446315 | 0 | 1446315 |  |  | 1446315 | 0 | 0
AE007181 | South Mission - South McAllen 69kv to 138kv transmission line rebuild | Hidalgo County, Texas | Rebuild the existing South Mission to South McAllen 69kv transmission line to a 138kv single circuit, double circuit capable, 6 mile line using bundled 1590 MCM ACSS on steel or concrete single pole structures | 2004-06-01 | 2004-12-01 |  | 2916000 |  |  |  | 85% | 69kV | 138kV | 6 miles | 1590 MCM ACSS | Concrete or steel single pole | Centerline Defined | 6 miles |  |  | Sub Rule 25.101 (c) (5) (B) | The line is located in TCC single certified and in MVEC (Magic Valley) single certified areas | 2916000 | 0 | 2916000 |  |  | 2916000 | 0 | 0
AE007171 | Bates - South Mission 69kv to 138kv line rebuild and termination relocation | Hidalgo County, Texas | Rebuild the existing 4.18 mile 69kv Bates to South Mission transmission line to a 138kv line using 1590 MCM ACSS on steel or concrete single pole structures, and relocate the West end of the line termination point from Bates 500' to the south to the Frontera switching station | 2004-06-01 | 2004-12-01 |  | 2127000 |  |  |  | 40% | 69kV | 138kV | 4.18 miles | 1590 MCM ACSS | Concrete or steel single pole | Centerline Defined | 4.18 miles |  |  | Sub Rule 25.101 (c) (5) (B) | The line is located in TCC single certified areas | 2127000 | 0 | 2127000 |  |  | 2127000 | 0 | 0
4024691301 | McColl - North McAllen 6.8 mile 138kv transmission line reconductor | Hidalgo County, Texas | Reconductor the approximately 6.8 miles of existing 138kv and convert the existing 69kv to 138kv which will result in a double circuit 138kv from McColl to North McAllen. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Poles will remain the same. | 2004-11-20 | 2004-12-31 |  | 1914000 |  |  |  | 87% | 138 kV and 69 kV | 138 kV both circuits | 6.8 miles | Drake 795 MCM ACSS | Wood Single Poles | Centerline Defined | 6.8 miles |  |  | Sub Rule 25.101 (c) (5) (B) | The line is located in TCC single certified area. On hold due to landowner opposition and City of McAllen concerns. | 1914000 | 0 | 1914000 |  |  | 1914000 | 0 | 0
4024696001 | Polk - Hall Acres 2.73 mile 138-kV transmission line rebuild and reconductor | Hidalgo County, Texas | Reuild and reconductor the approximately 2.73 miles of existing 138-kV from Polk Ave. to Hall Acres. The old conductor is 336 ACSR and the new conductor will be 795 ACSS. Wood structures will be replaced with steel structures. | 2004-09-15 | 2004-12-15 |  | 1352003 |  |  |  | 99% | 138 kV |  | 2.73 miles | Drake 795 MCM ACSS | Steel single pole | Centerline Defined | 2.73 miles |  |  | Sub Rule 25.101 (c) (5) (B) | The line is located in AEP-TCC single certified and in AEP-TCC / MVEC dual certified territory | 1352003 | 0 | 1352003 |  |  | 1352003 | 0 | 0
40389465 | N McAllen - W. McAllen 138kV at FM 2220 | Hidalgo County, Texas | Relocate 16 structures for road improvement | 2004-07-15 | 2004-10-01 |  | 418000 |  |  |  | 5% | 138kV |  | .76 miles | 795 AAC 37 strand | Steel pole | Cenerline Defined | 0.76 |  |  | Sub Rule 25.101 (c) (5) (F) | Relocation located in public Right-Of-Way acquired by TXDot | 418000 | 0 | 418000 |  |  | 418000 | 0 | 0
40203341 | Rebuild Rincon-Rockport 138-kV Line | Aransas, San Patricio | Rebuild the 15-mile Rincon-Rockport 138-kV transmission line from 4/0 on wood H-Frames to 795 ACSR on single steel poles. A relocation of one structure is also included at the request of TXDOT for a State Highway 188 expansion. | 2004-07-09 | 2004-12-31 | 2004-12-31 | 9930343 |  |  |  | 100% | 138-kV |  | 15.04 | 795 ACSR/AW | single steel pole | centerline | 15.04 | 100 | 0.22 | Sub. Rule 25.101(c)(5)(B) & (c)(5)(F) | Relocation will result in 22 additional feet in overall length. | 9930343 | 0 | 9930343 |  |  | 9930343 | 0 | 0
40306673 | Roma Tap Substation | Starr | Replace 3 switches with 3-breaker ring bus | 2004-07-12 | 2005-01-21 |  | 1677000 |  |  |  | 100% | [9 empty] | Pursuant to Subst. Rule 25.83 (a)(3) |  | 1677000 | 0 | 1677000 |  |  | 1677000 | 0 | 0
25188829 | Asherton-Conoco Tap Rebuild | Dimmit, Maverick | Rebuild the 33-mile Asherton-Conoco Tap 138kV transmission line section from 4/0 on wood H-Frames to 795 ACSR on single steel poles. | 2004-09-27 | 2005-06-15 |  | 13569156 |  |  |  | 25% | 138kV |  | 33 miles | 795ACSR | single steel pole | centerline | 33 mi. | 100* | 0.3 | Sub. Rule 25.101(c)(5)(B) | *- Existing 50 foot easement on one property owner can have line reconstructed with increased nos. of poles. Working to provide property owner an option to reduce nos. of poles by increasing width. | 13569156 | 0 | 13569156 |  |  | 13569156 | 0 | 0
40296509 | Roma-Garceno Rebuild | Starr | Rebuild and convert 5.34 miles of existing 69kV line to 138kV. | 2005-02-07 | 2005-04-01 |  | 2340000 |  |  |  |  | 69kV |  | 5.34 | 795ACSR | single steel pole | undefined | 5.34 |  |  | Sub.Rule 25.101(c)(5)(B)(i) |  | 2340000 | 0 | 2340000 |  |  | 2340000 | 0 | 0
4024695401 | Magic Valley Pharr - Pharr 3.57 mile 138-kV transmission line reconductor and upgrade | Hidalgo County, Texas | Reconductor the approximately 3.57 miles of existing 138kv from Magic Valley Pharr to North Pharr. The old line is 795 ACSR conductor and the new line will be 795 ACSS conductor. Most of the poles will remain the same. | 2005-03-24 | 2005-04-27 |  | 721169 |  |  |  | 2% |  |  | 3.57 miles | Drake 795 MCM ACSS | Wood Single Poles | Centerline Defined | 3.57 miles |  |  | Sub. Rule 25.101(c)(5)(B) | The line is located in TCC single certified and in TCC / MVEC (Magic Valley) dual certified areas | 721169 | 0 | 721169 |  |  | 721169 | 0 | 0
25188829 STAFF A | Escondido Cut In-Conoco Tap | Maverick | Rebuild 17.94 miles of Conoco Tap to Escondido Cut-In 138kV transmission line from 4/0 on wood H-frames to 795ACSR on single steel poles. | 2005-03-28 | 2006-12-08 |  | 7812545 |  |  |  | 0% | 138kV |  | 17.94 | 795ACSR | single steel pole | centerline | 17.94 | centerline* |  | Sub. Rule 25.101(c)(5)(B) | *Existing 50 foot easement on three property owners can have line reconstructed with increased nos. of poles. Working to provide property owners an option to reduce nos. of poles by increasing width. | 7812545 | 0 | 7812545 |  |  | 7812545 | 0 | 0
40211303 | Rebuild and Upgrade Rockport - Fulton 69-kV line | Aransas County, Texas | Rebuild and upgrade the 7.4 mile Rockport to Fulton 69-kV transmission line from 4/0 on wood H-frame structures to 795 ACSR on single pole steel structures. | 2005-02-26 | 2005-06-02 |  | 4665766 |  |  |  |  | 69 kV | 138 kV | 7.4 | 795 ACSR/AW | Steel single pole | Centerline | 7.4 |  |  | Sub Rule 25.101 (c) (5) (B) | Line is located in TCC singly certificated territory. | 4665766 | 0 | 4665766 |  |  | 4665766 | 0 | 0
40448486 | Key 138kV Switch Station and 138kV Hairpin T-Line | Palmhurst, Texas | Construct approximately .31 miles of double circuit 138kV line using 1272 MCM ACSR on steel pole sturctures to serve new Key Switching Station. | 2005-04-11 | 2005-09-11 |  | 1245500 | [5 empty] | 138 kV | .62 miles | 1272 MCM ACSR | Steel single pole |  |  | 100 ft. | .31 miles | Sub Rule 25.101 (c) (5) (A) | The line is located in TCC/MVEC (Magic Valley) dual certified area. Consent obtained. | 1245500 | 0 | 1245500 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 111011672 | 111011672
[24 empty] | 0 | 22 | 22 | Project Count
[24 empty] | Completed | Active | Total
Note on A25: Allen Steven Boling: STAFF ADDED TEXT TO PROJECT NUMBER TO CREATE A UNIQUE PROJECT SINCE NUMBER IS ALREADY BEING USED IN THIS REPORT.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on W5: aboling: PUC STAFF RETAINED PROJECT IN AEPC RATHER THAN LCRA FOR REPORTING PURPOSES. ACTUAL FINAL COST ($30,112,264) WAS REPORTED IN AUGUST LCRA REPORT AND STAFF RE-ENTERED IN THE AEPC REPORT AS A COMPLETED PROJECT. COMMENT FROM LCRA JULY REPORT IS ADDED HERE.
Note on X3: aboling: PUC Staff: LCRA July report shows this project 100% complete. Formula deleted to reflect that report. Projects remain only for informational purposes.
Note on X4: aboling: PUC Staff: LCRA July report shows this project 100% complete. Formula deleted to reflect that report. Projects remain only for informational purposes.

## AEPN
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
24028549 24908005 40079168 | N McCamey- McCamey - Tippett | Upton, Crockett, and Pecos Counties | Rebuild 13.46 miles of 69kV line to 138 kV | 2002-08-26 | 2003-02-21 | 2003-02-21 | 4990000 |  |  |  | 99% | 69kV | 138kV | 13.46 mi. | Bundled 795 ACSR | Concrete single pole | center-line | 13.46 |  |  | Exempt per Subst. Rule 25.101(c)(2)(C)(ii) |  | 4990000 | 0 | 4990000 |  |  | 4990000 | 0 | 0
40066293 | N McCamey - LCRA Crane Tap Reconductor | Upton County, Texas | Rebuild 25 miles of existing N McCamey to McElroy 69kV to 138kV | 2003-02-05 | 2003-07-15 | 2003-07-15 | 8748410 |  |  |  | 99% | 69kV | 138kV | 25 mi. | Bundled 795 ACSR | Concrete single pole | center-line | 25 mi. |  |  | Exempt per Subst. Rule 25.101(c)(2)(C)(ii) | Notice sent to SWTEC | 8748410 | 0 | 8748410 |  |  | 8748410 | 0 | 0
24028557 24907990 40079274 | Tippet to W Yates Tap Reconductor | Pecos/Crockett Counties, Texas | Rebuild 9.98 miles of 69kV to 138kV | 2002-12-01 | 2003-05-12 | 2003-05-12 | 3803891 |  |  |  | 99% | 69kV | 138kV | 9.98 mi | Bundled 795 ACSR | Concrete single pole | center-line | 9.98 mi |  |  | Exempt per Subst. Rule 25.101(c)(2)(C)(ii) | Notice sent to Oncor | 3803891 | 0 | 3803891 |  |  | 3803891 | 0 | 0
40078782 | W Yates Tap - West Ytes Pump | Pecos County | Rebuild existing 69kV H-Frame and single pole line with single concrete pole, double circuit, 2-795 ACSR construction. | 2003-06-30 | 2003-08-29 | 2003-08-29 | 2019654 |  |  |  | 99% | 69kV | 138kV | 4.23 | Bundled 795 ACSR | Concrete single pole | center-line | 4.23 |  |  | Exempt per Subst. Rule 25.101(c)(2)(C)(ii) |  | 2019654 | 0 | 2019654 |  |  | 2019654 | 0 | 0
40081686 | W Yates Pump - Mesa View | Pecos County | Install approximately 300' of single circuit 2-795, 138kV line between existing poles, tying the MVS-MV line to the WYS-WYP line. The dead end structures will be installed when the lines are rebuilt. | 2003-11-12 | 2003-12-15 | 2004-01-04 | 200000 |  |  |  | 99% |  | 138kV | 0.1 | Bundled 795 ACSR | Concrete single pole | center-line | 0.1 |  |  | Exempt per Subst. Rule 25.101(c)(2)(C)(ii) | Sectionaliz-ing switches added to design | 200000 | 0 | 200000 |  |  | 200000 | 0 | 0
40079178 | Rio Pecos - Crane 69 kV Rebuild | Crane and Crockett Counties | Rebuild existing 69kV H-Frame and single pole line with single concrete pole, double circuit capable, 2-795 ACSR construction. | 2003-09-08 | 2003-02-23 | 2004-03-26 | 9721600 |  |  |  | 99% | 69kV | 138kV | 23 | Bundled 795 ACSR | Concrete single pole | center-line | 23 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice sent SWTEC, Oncor, Crane County Airport and landowners | 9721600 | 0 | 9721600 |  |  | 9721600 | 0 | 0
40079178a | Crane Line Extension | Crane County | Extension of the Rio Pecos - Crane 69 kV rebuild into the new LCRA Transmission Services Corp. Crane Switching Station. | 2003-09-08 | 2004-01-16 | 2004-03-26 | 358768 |  |  |  | 99% |  | 138kV | 0.56 | Bundled 795 ACSR | Concrete single pole(double ckt. capable) | 0 | 0 | 70'-80' | 0.56 | Exempt per Subst. Rule 25.101(c)(5)(A) | Consent has been given by the only impacted landowner. | 358768 | 0 | 358768 |  |  | 358768 | 0 | 0
24914185 | S. Abilene to Eskota Reconductor | Tayor/Nolan Counties, Texas | Reconductor and rebuild approximately 25.7 miles of existing 138kV transmission line. The old line is 40 ACRS on wood H-frame structures. The new line will be single pole structure with 795 ACSR conductor. | 2003-09-05 | 2004-03-01 | 2003-12-19 | 9275000 |  |  |  | 99% | 138kV | 138kV | 25.7 | Single 795, MCM ACSR and 3/8 EHS | Concrete Single Poles | Center-line Defined | 25.7 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | This line is located in dual certified service area with Taylor Electric CoOp. | 9275000 | 0 | 9275000 |  |  | 9275000 | 0 | 0
24907967 | Crane to McElroy Cut-In 69 kV | Crane and Upton Counties | Construct 1.57 miles of 69 kV from Crane to the McElroy/N. McCamey Cut-In | 2004-05-01 | 2004-06-04 | 2004-09-14 | 748326 |  |  |  | 99% |  | 69kV | 1.57 | 795 ACSR | Concrete single pole |  |  | 80' | 1.57 |  | Docket No. 27484 | 748326 | 0 | 748326 |  |  | 748326 | 0 | 0
40078850, 24907989 | Mesa View - Mesa View Switch 138kV Line | Pecos County, TX | Rebuild the existing Mesa View - Mesa View Switch 138kV H-Frame line with single concrete pole construction, double circuit capable, 2-795 ACSR drake conductors (One circuit installed initially) | 2004-01-12 | 2004-03-21 | 2004-03-21 | 2267387 |  |  |  | 99% | 138kV | 138kV | 5.7 | Bundled 795 ACSR | Concrete single pole (double ckt. Capable) | center line | 5.7 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice sent to SWTEC and landowners | 2267387 | 0 | 2267387 |  |  | 2267387 | 0 | 0
40079259 24028552 24908016 | Rio Pecos - N McCamey | Crane, Crockett, Upton Counties | Rebuild the existing 138kV H-Frame line with single concrete pole construction, double circuit capable, 2-795 ACSR drake conductors | 2004-03-01 | 2004-05-29 | 2004-05-20 | 3932021 |  |  |  | 99% | 138 | 138 | 9.67 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) | center line | 9.67 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice to sent to Upton County Commissioners and landowners | 3932021 | 0 | 3932021 |  |  | 3932021 | 0 | 0
40078866 24028551 24908020 | Rio Pecos - Mesa View 138 | Crockett, Pecos Counties | Rebuild the existing 138kV H-Frame line with single concrete pole construction, double circuit capable, 2-795 ACSR drake conductors | 2004-03-15 | 2004-09-14 | 2004-09-13 | 11401500 |  |  |  | 99% | 138 | 138 | 27.13 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) | center line | 27.13 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice sent to SWTEC and landowners | 11401500 | 0 | 11401500 |  |  | 11401500 | 0 | 0
40078884 24028553 24908021 | Mesa View - Ft. Lancaster | Pecos County | Rebuild the existing 138kV H-Frame line with single concrete pole construction, double circuit capable, 2-795 ACSR drake conductors | 2004-09-03 | 2005-01-28 | 2005-01-15 | 8342686 |  |  |  | 98% | 138 | 138 | 19.8 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) | center line | 19.8 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice sent to SWTEC and landowners | 8342686 | 0 | 8342686 |  |  | 8342686 | 0 | 0
40079205 | Rio Pecos - Crane Line Extension | Crane County | Extend the existing 138kV H-Frame line with single concrete or steel pole construction, double ckt. capable, 2-795 ACSR drake conductors into LCRA Crane Switching Station | 2003-11-17 | 2003-11-21 | 2003-11-21 | 900000 |  |  |  | 99% | 138 | 138 | 0.5 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) | center line | 0.07 | center line | 0.5 | Exempt per Subst. Rule 25.101(c)(5)(A) | Notice sent to Oncor and Crane County Airport. Landowner consent. | 900000 | 0 | 900000 |  |  | 900000 | 0 | 0
40289972 | Crane Bus-Tie Extension | Crane County | Extend 138kV line with single concrete pole construction, 795 ACSR drake conductors from AEP Texas North Crane Substation to LCRA Crane Switching Station | 2003-11-17 | 2003-11-21 | 2003-11-21 | 200000 |  |  |  | 99% | 138 | 138 | 0.15 | 795 ACSR | Concrete single pole | center line | 0.07 | center line | 0.15 | Exempt per Subst. Rule 25.101(c)(5)(A) | Notice sent to Oncor and Crane County Airport. Landowner consent. | 200000 | 0 | 200000 |  |  | 200000 | 0 | 0
40162899 | Twin Buttes / Big Lake Cut-in Circuit | Tom Green Coiunty | Buid 9.65 mils of bundled 795 ACSR circuit from Twin Buttes Switching Station to cut-in 138kV line from Big Lake Substation. Circuit will be located on LCRA Transmission Services structures | 2004-04-05 | 2004-08-15 | 2004-08-21 | 1041462 |  |  |  | 99% |  | 138 | 9.65 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) |  |  | center line | 9.65 |  | Docket No. 27180 | 1041462 | 0 | 1041462 |  |  | 1041462 | 0 | 0
23426044 | Big Lake/SAPS Cut-in - SAPS rebuild | Tom Green Coiunty | Reconductor and rebuild approximately 7.33 miles of existing 138kV transmission line. The new line will be single pole structure with 2-795 ACSR conductor. | 2004-04-26 | 2004-08-15 | 2004-08-21 | 3801606 |  |  |  | 99% | 138 | 138 | 7.33 | Bundled 795 ACSR | Concrete or steel single pole (double ckt. Capable) | center line | 7.33 |  |  | Exempt per Subst. Rule 25.101(c)(5)(B) | Notice sent to CVEC and landowners | 3801606 | 0 | 3801606 |  |  | 3801606 | 0 | 0
24908014 40288951 40288918 40288943 40288953 | Friend Ranch Substation terminal addition | Crockett County | Add terminal at Friend Ranch for new LCRA Ft. Lancaster to Friend Ranch 138kV line | 2005-02-14 | 2005-03-15 |  | 568000 |  |  |  | 75% | [9 empty] | Pursuant to Subst. Rule 25.83 (a)(3) |  | 568000 | 0 | 568000 |  |  | 568000 | 0 | 0
40449023 | Presidio Relocation | Presidio County | Relocate six structure for the city to widen Hord Street | 2004-12-15 | 2005-01-01 |  | 266000 |  |  |  | 0% | 69 |  | 0.55 | #2 ACSR | Steel Single Pole | Center Line | 0.55 | Cener Line | 0 | Pursuant to Subst. Rule 25.101(c)(5)(F) | No new ROW required. | 266000 | 0 | 266000 |  |  | 266000 | 0 | 0
40385791 | Munday - Throckmorton | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2004-12-06 | 2005-01-31 |  | 490000 |  |  |  | 99% | 69 |  | 0.424 | 4/0 ACSR 6/1 | single pole, single and double ckt, concrete | center line | 0.424 | 60 | 0.424 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained | 490000 | 0 | 490000 |  |  | 490000 | 0 | 0
40385795 | Munday - Haskell | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2004-12-06 | 2005-01-31 |  | 0 |  |  |  | 0% | 69 |  | 0.424 | 4/0 ACSR 6/1 | single pole, single and double ckt, concrete | center line | 0.424 | 60 | 0.424 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained
40385983 | East Munday - Munday | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2005-01-06 | 2005-01-31 |  | 566000 |  |  |  | 5% | 138 |  | 0.18 | 795 ACSR 26/7 | concrete, 3 pole, double circuit | center line | 0.18 | 60 | 0.18 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained | 566000 | 0 | 566000 |  |  | 566000 | 0 | 0
40386074A | Munday - Baylor County Line East of Goree | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2004-12-06 | 2005-01-31 |  | 242880 |  |  |  | 99% | 69 |  | 0.25 | 4/0 ACSR 6/1 | single pole, concrete | center line |  | 60 | 0.25 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained | 242880 | 0 | 242880 |  |  | 242880 | 0 | 0
40386081 | East Munday - Lake Pauline | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2005-01-06 | 2005-02-18 |  | 133100 |  |  |  | 99% | 138 |  | 0.1 | Bundled 4/0 ACSR 6/1 | concrete h-frame | center line |  |  |  | Pursuant to Subst. Rule 25.101(c)(5)(F) | No new ROW required. | 133100 | 0 | 133100 |  |  | 133100 | 0 | 0
40394705 | East Munday - Paducah Clare St. | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2005-01-06 | 2005-02-18 |  | 108000 |  |  |  | 99% | 138 |  | 0.1 | 477 ACSR 26/7 | concrete h-frame | center line |  |  |  | Pursuant to Subst. Rule 25.101(c)(5)(F) | No new ROW required. | 108000 | 0 | 108000 |  |  | 108000 | 0 | 0
40394718 | Munday - Baylor County Line Switch | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2004-12-06 | 2005-01-31 |  | 45000 |  |  |  | 99% | 69 |  | 0.1 | 4/0 ACSR 6/1 | single pole, concrete | center line |  |  |  | Pursuant to Subst. Rule 25.101(c)(5)(F) | No new ROW required. | 45000 | 0 | 45000 |  |  | 45000 | 0 | 0
40386074B | Munday - Baylor County Line West of Goree | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2005-02-14 | 2005-03-15 |  | 364320 |  |  |  | 0% | 69 |  | 0.75 | 4/0 ACSR 6/1 | single pole, concrete | center line |  | 60 | 0.75 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained | 364320 | 0 | 364320 |  |  | 364320 | 0 | 0
40386069 | Munday - Baylor County Line at Munday | Knox County | One portion of the work required to relocate approximately 40 structures near Munday, TX impacted by the relocation of a section of US 277 | 2005-01-24 | 2005-02-11 |  | 467600 |  |  |  | 99% | 69 |  | 0.75 | 4/0 ACSR 6/1 & 477 ACSR 26/7 | single pole, concrete | center line |  | 60 | 0.75 | Pursuant to Subst. Rule 25.101(c)(5)(F) | 100% consent obtained | 467600 | 0 | 467600 |  |  | 467600 | 0 | 0
40424168 & 40474050 | Santa Anna-Bangs | Coleman County | Rebuild existing 69kV single wood pole line with double circuit 138/69 kV single steel pole construction, 795 ACSR conductor | 2005-01-24 | 2005-06-07 |  | 5148800 |  |  |  | 0% | 69 | 69 and138 | 7.21 | 795 ACSR | Single Pole Steel, double circuit | center line | 7.21 | center line | 7.21 | Pursuant to Subst. Rules 25.101(c)(5)(B) and 25.101(c)(5)(C) | 100% consent obtained | 5148800 | 0 | 5148800 |  |  | 5148800 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 80152011 | 80152011
[24 empty] | 0 | 28 | 28 | Project Count
[24 empty] | Completed | Active | Total
Note on A22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on B22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on C22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on D22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on E22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on F22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on G22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on I22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on J22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on K22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on L22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on M1: aboling: If applicable.
Note on M22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on N1: aboling: If applicable.
Note on N22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on O22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on P22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on Q22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on R22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on S22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on T22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on U22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on V22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.
Note on W22: Allen Steven Boling: THIS PROJECT IS REDUNDANT.

## BEPC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
00002 | Booneville to Hearne | Robertson & Brazos County | Rebuilding of approx. 23 miles of 138 kV 795 MCM line from existing Booneville sub. to existing Hearne sub. | 2003-06-01 | 2003-08-15 |  | 7989950 |  |  |  | 0% | 138 |  | 23 | 795 MCM | Single Pole Concrete | 60 | 23 |  |  | 25.101(c)(2)(C)(ii) |  | 7989950 | 0 | 7989950 |  |  | 7989950 | 0 | 0
91037 | Bridgeport - Crafton | Wise County | Construct 8.4 miles of SC & DC line built for 138kV but operated at 69kV. Constructed to avoid mining operations. | 2003-04-01 | 2003-08-25 |  | 3231600 |  |  |  | 100% | 69 | 138 | 8.4 | 4/0 ACSR | Single Pole Concrete | 60 | 5.1 |  |  | Docket No. 25288 |  | 3231600 | 0 | 3231600 |  |  | 3231600 | 0 | 0
01006 | North Texas - Cottondale | Parker & Wise County | Rebuild approx. 26.8 miles of existing H-frame 4/0 ACSR 69 kV line with single pole 138 kV, 795 MCM ACSR construction. In addition, BEPC's Willow substation will be converted to 138 kV operation. | 2004-03-01 | 2004-06-01 |  | 7081200 |  |  |  | 100% | 69 | 138 | 26.8 | 795 MCM | Single Pole Concrete or Steel | 60 | 26.8 |  |  | 25.101(c)(2)(C)(ii) |  | 7081200 | 0 | 7081200 |  |  | 7081200 | 0 | 0
98051 | Cedar Valley | Bell County | Construct a new single-pole concrete and/or steel 138 kV 795 MCM transmission line and in-line 138/25 9375 kVA substation with two 3-phase bays and one spare bay. | 2005-08-01 | 2005-12-31 |  | 6372650 |  |  |  | 0% | NA | 138 | 13.8 | 795 ACSR double circuit | Single Pole Concrete or Steel | NA | NA | 70 | 6.9 | Docket No. 27894 | CCN Application Filed on June 5, 2003 | 6372650 | 0 | 6372650 |  |  | 6372650 | 0 | 0
0208445 | Reno - Cottondale Switch | Wise and Parker County | Rebuild approx. 19.25 miles of existing 69 kV line with 138 kV 959 ACSS conductor. Convert Keeter 69 kV sub. to 138 kV. | 2004-02-16 | 2004-09-18 |  | 10821550 |  |  |  | 100% | 69 | 138 | 19.25 | 959 ACSS | Single Pole Concrete or Steel | 60 & 100 | 19.25 |  |  | 25.101(c)(5)(B)(i) | Affidavit attached with filing. | 10821550 | 0 | 10821550 |  |  | 10821550 | 0 | 0
02012 | Fairview - Aledo | Hood & Parker County | Construct approximately 26 miles of new single-pole 138 kV 795 MCM transmission line from the existing radial fed BEPC Fairview substation to the existing radial fed BEPC Aledo substation. In addition, this project will include rebuilding approximately 5.8 miles of existing transmission line from the BEPC Waples substation to the BEPC Fairview substation. Also, included in the project is the construction of a switching station at Dicey and the addition of a 138 kV breaker at Waples substation. | 2005-06-15 | 2006-02-15 |  | 10752500 |  |  |  | 0% | NA | 138 | 26 | 795 MCM | Single Pole Concrete or Steel | NA | NA | 70 | 26 | Docket No. 28254 | CCN Application Filed on August 15, 2003 | 10752500 | 0 | 10752500 |  |  | 10752500 | 0 | 0
00005 | Cross Timbers | Denton County | Construct approx. 4.0 miles of 138 kV double circuit 1590 ACSR single pole concrete structures adjacent to Oncor Transmission's existing 345 kV line west of Grapevine Lake near the town of Flower Mound, Texas to connect teh proposed Cross Timbers Substation to the Brazos System | 2004-10-04 | 2005-02-01 |  | 8082900 |  |  |  | 65% | NA | 138 | 8 | 1590 ACSR | Single Pole Concrete or Steel | NA | NA | 70 or as needed | 4 | Docket No. 27144 | CCN Filed Dec. 20, 2002. I apparently failed to include this in previous construction rpts. | 8082900 | 0 | 8082900 |  |  | 8082900 | 0 | 0
02079 | Tin Top to Brock | Parker County | Rebuild approx. 8.7 miles of existing 69 kV line from Tin Top sub to Brock sub. | 2004-05-24 | 2004-11-15 |  | 2650450 |  |  |  | 100% | 69 | 138 | 8.70 mi | 795 MCM | Single Pole Concrete or Steel | 60-100 | 8.7 |  |  | 25.101(c)(5)(B) | Affidavit attached with filing. | 2650450 | 0 | 2650450 |  |  | 2650450 | 0 | 0
02084 | Bowie - St. Jo | Montague & Cooke County | Reconductor approximately 19 miles of existing 4/0 ACSR 138 kV transmission line with 795 mcm conductor. Upgrade Bowie and St. Jo to accommodate larger conductor. Replace Hardy Tap GOAB | 2004-02-15 | 2004-05-15 |  | 6007250 |  |  |  | 100% | 138 |  | 19 | 795 MCM | Single Pole Concrete or Steel | 60 & 100 | 19 |  |  | 25.101(c)(5)(B) | Affidavit attached with filing. | 6007250 | 0 | 6007250 |  |  | 6007250 | 0 | 0
96023 | Ben Hur to Perry and Ben Hur to Prairie Hill | Limestone & Falls | Rebuild approx. 11.4 miles of existing 69 kV from Ben Hur to Prairie Hill. Reconductor approx. 12.1 miles of existing 69 kV from Ben Hur to Perry and operater at 138 kV. Convert Ben Hur, Perry, and Prairie Hill to 138 kV operation. SCADA and Comm equip and motor operated switches at Dawson. | 2004-03-11 | 2004-11-01 |  | 7374350 |  |  |  | 100% | 69 | 138 | 23.50 mi | 795 MCM | Single Pole Concrete or Steel | 60-100 | 23.5 |  |  | 25.101(c)(5)(B) | Affidavit attached with filing. | 7374350 | 0 | 7374350 |  |  | 7374350 | 0 | 0
0208432 | Generation Plant to Wise Co. Switch | Jack and Wise | Construct a new single-pole concrete and/or steel single circuit 138 kV 959 MCM ACSS line from the new Jack Co. Generation Plant to a new Wise County Switch. The line is approximately 20 miles in length. | 2005-11-01 | 2006-05-01 |  | 7531850 |  |  |  | 0% | NA | 138 | 20 | 959 MCM ACSS | Single Pole Concrete or Steel | NA | NA | 70 | 20 | Docket No. 29020 | CCN Filed Jan. 7, 2004 | 7531850 | 0 | 7531850 |  |  | 7531850 | 0 | 0
0208426 | Generation Plant to Willow | Jack and Wise | Construct a new single-pole concrete and/or steel single circuit 138 kV 959 MCM ACSS line from the new Jack Co. Generation Plant to BEPC's existing Willow Substation with a 70 foot ROW for approx. 8.2 miles | 2004-08-15 | 2004-12-20 |  | 2268575 |  |  |  | 100% | NA | 138 | 8.2 | 959 MCM ACSS | Single Pole Concrete or Steel | NA | NA | 70 | 8.2 | Docket No. 29158 | Brazos has purchased options on easements for this project and attached to CCN application filed on Jan15, 2004 | 2268575 | 0 | 2268575 |  |  | 2268575 | 0 | 0
0208430 | Generation Plant to Joplin | Jack County | Construct a new single-pole concrete and/or steel, single circuit 138kV 795 MCM ACSR line from the Jack Co. Generating Plant to BEPC's existing Joplin Substation. The line is approximately 3.20 miles in length. | 2004-08-23 | 2004-12-10 |  | 990100 |  |  |  | 100% | 69 | 138 | 3.20 mi | 795 MCM ACSR | Single Pole Concrete or Steel | 60 | 3.2 | 70 | 3.2 | Docket No. 29198 | Brazos is purchasing options on easements for this project and will include them in this application. The CCN was filed on Jan 30, 2004. | 990100 | 0 | 990100 |  |  | 990100 | 0 | 0
0208431 | Generation Plant to Cottondale Switch | Jack & Wise | Construct a new single-pole, concrete and/or steel, single circuit 138kV 959MCM ACSS line from the Jack Co. Generating Plant to BEPC's existing Cottondale Switch. The line is approximately 5.20 miles in length. | 2004-10-01 | 2005-04-01 |  | 1981450 |  |  |  | 55% | NA | 138 | 5.2 | 959 MCM ACSS | Single Pole Concrete or Steel | NA | 5.2 | 110 | 5.2 | Docket No. 29186 | Brazos has pirchased options for easements for this project and they where included in the application. This CCN was filed on Feb 13, 2004 | 1981450 | 0 | 1981450 |  |  | 1981450 | 0 | 0
0208428 | Generation Plant to Cottondale Sw Rebuild | Jack & Wise | Rebuild approximately 5.20 miles of 138kV line from the Jack Co. Generating Plan to BEPC's existing Cottondale SW. with single concrete and/or steel poles. | 2004-10-01 | 2005-04-01 |  | 1981450 |  |  |  | 55% | 69 | 138 | 5.20 mi. | 959 MCM ACSS | Single Pole Concrete or Steel | 70 | 5.2 | 70 | 5.2 | 25.101(c)(5)(B) | Affidavit at a later date closer to scheduled construction start | 1981450 | 0 | 1981450 |  |  | 1981450 | 0 | 0
201120 | Grandview to Happy Hills Switch | Johnson | Rebuild 9.8 Miles of line from Grandview to Happy Hill Switch with 1033 MCM conductor 138kv single circuit construction | 2004-12-01 | 2005-05-01 |  | 3860000 |  |  |  | 5% | 69 | 138 | 9.8 mi. | 1033 MCM ACSR | Single Pole Concrete or Steel | NA | 9.8 | 70 | 9.8 | 25.101(c)(5)(B) | Affidavit attached with filing | 3860000 | 0 | 3860000 |  |  | 3860000 | 0 | 0
300420 | Spring to St. Jo | Cooke | Rebuild 23.36 miles of line from St. Joe to Spring with 138kV 795MCM line | 2005-01-15 | 2005-06-15 |  | 6883750 |  |  |  | 0% | 69 | 138 | 23.36 | 795 MCM ACSR | Single Pole Concrete or Steel | NA | 23.36 mi. | 70 | 23.36 | 25.101(c)(5)(B) | Affidavit attached with filing. | 6883750 | 0 | 6883750 |  |  | 6883750 | 0 | 0
02004 | North Denton - Spring | Denton County | Rebuild 17.06 miles of line from North Denton to Spring with 795 MCM Conductor | 2005-03-15 | 2005-09-15 |  | 4895950 |  |  |  | 0% | 69 | 138 | 17.06 | 795 MCM ACSR | Single Pole Concrete or Steel | NA | 17.06 mi. | 70 | 17.06 mi. | 25.101(c)(5)(B) | Affidavit attached with filing. | 4895950 | 0 | 4895950 |  |  | 4895950 | 0 | 0
02001 | Gibbons Creek -College Station Sw. | Brazos | Rebuild 24.1 miles of line from Gibbons Creek - Carlos Sw. with 795 MCM ACSR and or 1433 ACSS | 2005-06-15 | 2005-12-15 |  | 10178150 |  |  |  | 0% | 69 | 138 | 24.1 mi | 795 MCM & 1433 ACSS | Single Pole Concrete or Steel | NA | 24.1 mi | 70 | 24.1 mi | 25.101(c)(5)(B) | Affidavit at a later date closer to scheduled construction start | 10178150 | 0 | 10178150 |  |  | 10178150 | 0 | 0
02084 Staff A | Bowie - Cottondale Sw. | Montague & Wise | Rebuild 30.61 niles of line from Bowie to Cottondale Sw. with 959 ACSS | 2005-06-15 | 2005-12-15 |  | 7263200 |  |  |  | 0% | 69 | 138 | 30.61 mi | 959 ACSS | Single Pole Concrete or Steel | NA | 30.61 mi | 70 | 30.61 mi | 25.101(c)(5)(B) | Affidavit at a later date closer to scheduled construction start | 7263200 | 0 | 7263200 |  |  | 7263200 | 0 | 0
4006 | Herane - Herane Southwest Rebuild | Robertson | Rebuild 4.18 miles of line from Hearne to Hearne Southwest with 795MCM | 2005-06-15 | 2005-12-15 |  | 1871250 |  |  |  | 0% | 69 | 138 | 4.18 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 4.18 mi | 70 | 4.18 mi | 25.101(c)(5)(B) | Affidavit at a later date closer to scheduled construction start | 1871250 | 0 | 1871250 |  |  | 1871250 | 0 | 0
0301820 | Powell - Meridian Rebuild | Bosque County | Rebuild 9.71 miles of line from Powell to Meridian with 795 ACSR Drake | 2005-11-01 | 2006-02-01 |  | 2913000 |  |  |  | 0% | 69 | 138 | 9.71 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 9.71 mi | 60 | 9.71 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 2913000 | 0 | 2913000 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 122983125 | 122983125
[24 empty] | 0 | 22 | 22 | Project Count
[24 empty] | Completed | Active | Total
Note on A21: Allen Steven Boling: STAFF MODIFIED PROJECT NUMBER TO CREATE A UNIQUE PROJEC NUMBER.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## CNP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
310 | I-10 Widening | Harris | Alteration of 138 kV Ckts. 73A and 81D within 200 feet of the existing facilities as requested by TxDOT for highway construction | 2003-10-10 | 2006-05-18 |  | 60590000 | 60590000 |  |  | 25% | 138 | NA | 11.6 | 3000 CU, 3500 CU | Steel Poles, Underground Cable | Street, 40 | 5.8 | 0-60 | 0.12 | 25.101(c)(2)(C)(v) | Actual cost to be reimbursed by TxDOT. | 60590000 | 0 | 60590000 |  |  | 60590000 | 0 | 0
361 | Karsten - Manvel Tap | Alvin, Iowa Colony, Manvel, Brazoria | Partial Rebuild of 69 kV Ckt. 53D | 2004-04-07 | 2004-09-21 |  | 1955000 | 2306000 | 2153852 | -6.598% | 100% | 69 | NA | 5.1 | 1433 ACSS | Steel Towers | 250-360 | 5.1 | NA | NA | 25.101(c)(5)(B) | Last time to report. | 2306000 | 2306000 | 0 |  |  | 2306000 | 0 | 0
361.1 | W.A. Parish - Oasis | Thompsons, Arcola, Fort Bend, Alvin, Iowa Colony, Manvel, Brazoria | Bundling, Partial Reconductor, and Partial Rebuild of 345 kV Ckt. 99B | 2004-02-23 | 2004-10-24 |  | 4320000 | 4406000 | 3474878 | -21.13% | 100% | 345 | NA | 19.8 | 2-795 ACSR, 2-927 ACAR, 2-1433 ACSS | Steel Towers | 200-3275 | 19.8 | NA | NA | 25.101(c)(5)(B) | Last time to report. Overhead allocations were lower than estimated. | 4406000 | 4406000 | 0 |  |  | 4406000 | 0 | 0
361.2 | Oasis Substation | Manvel, Brazoria | 345 kV Service to Oasis Substation within one mile of Ckts. 99B and 99A | 2004-02-16 | 2004-11-09 |  | 1830000 | 1622000 | 1639815 | 1.098% | 100% | 345 | NA | 0.5 | 2-795 ACSR, 2-1433 ACSS | Steel Towers | Substation Property, 200 | 0.2 | NA | NA | 25.101(c)(5)(A) | Last time to report. | 1622000 | 1622000 | 0 |  |  | 1622000 | 0 | 0
484 | CNP - TNP Tie | Texas City, Galveston | Reconductor 138 kV Ckt. 01X | 2004-03-01 | 2005-03-01 |  | 120000 | 126000 |  |  | 50% | 138 | NA | 0.4 | 2-959.6 ACSS | Steel Towers | 2400-2500 | 0.4 | NA | NA | 25.101(c)(5)(B) |  | 126000 | 0 | 126000 |  |  | 126000 | 0 | 0
888.2 | P.H. Robinson - West Galveston | Texas City, Dickinson, League City, Santa Fe, La Marque, Hitchcock, Galveston, Galveston | Routine maintenance of 138 kV Ckt. 93B | 2004-08-30 | 2005-01-11 |  | 500000 | 643000 |  |  | 99% | 138 | NA | 44.3 | 2-795 AAC, 2-795 ACSR, 795 ACSR, 795 AAC, 2-397 ACSR | Steel Towers, Wooden H-Frames, Wood Poles | Street, 50-2500 | 44.3 | NA | NA | 25.83 (a)(3) | Construction Complete. | 643000 | 0 | 643000 |  |  | 643000 | 0 | 0
548 | Spring ISD Relocation | Houston, Harris | Relocation of a portion of 138 kV Ckts. 66D and 67C at the request of and at the expense of Spring ISD on ROW provided by Spring ISD | 2004-09-15 | 2005-02-28 |  | 700000 | 896000 |  |  | 95% | 138 | NA | 1.7 | 2-795 AAC, 795 AAC | Concrete Poles | NA | NA | 125 | 0.85 | 25.101(c)(5)(D) | Actual cost to be reimbursed by Spring ISD. | 896000 | 0 | 896000 |  |  | 896000 | 0 | 0
369 | Bellaire - Brays | Houston, Bellaire, West University Place, Harris | Reconductor and Partial Rebuild of 138 kV Ckt. 09B | 2004-10-11 | 2005-01-12 |  | 500000 | 675000 |  |  | 99% | 138 | NA | 3.1 | 2-959.6 ACSS | Steel Towers | 130-270 | 3.1 | NA | NA | 25.101(c)(5)(B) | Construction Complete. | 675000 | 0 | 675000 |  |  | 675000 | 0 | 0
888.4 | Flewellen - Peters | Fulshear, Fort Bend, Brookshire, Waller, San Felipe, Sealy, Austin | Routine maintenance of 138 kV Ckt. 25E | 2004-12-20 | 2005-03-10 |  | 480000 | 863000 |  |  | 65% | 138 | NA | 26.5 | 795 AAC | Wooden H-Frames, Steel Towers | 80-300 | 26.5 | NA | NA | 25.83 (a)(3) |  | 863000 | 0 | 863000 |  |  | 863000 | 0 | 0
888.5 | Alvin - La Marque | Alvin, Brazoria, Santa Fe, La Marque, Hitchcock, Galveston | Routine maintenance of 69 kV Ckt. 53B | 2004-09-04 | 2004-12-23 |  | 260000 | 285000 |  |  | 99% | 69 | NA | 20.7 | 4/0 ACSR, 795 AAC, 795 ACSR, 397 ACSR | Wooden H-Frames, Concrete/Steel/Wood Poles, Steel Towers | Street, 22-106 | 20.7 | NA | NA | 25.83 (a)(3) | Construction Complete. | 285000 | 0 | 285000 |  |  | 285000 | 0 | 0
598 | Fry Road | Harris | Alteration of 345 kV Ckts. 98C and 98D as requested by Harris County for road construction | 2004-09-27 | 2004-12-02 |  | 170000 | 170000 |  |  | 99% | 345 | NA | 0.2 | 2-927 ACAR | Steel Towers | 255 | 0.14 | NA | NA | 25.101(c)(5)(F) | Construction Complete. Actual cost to be reimbursed by Harris County. | 170000 | 0 | 170000 |  |  | 170000 | 0 | 0
603 | Klein - Kluge - Cameron | Houston, Harris | Partial Reconductor and Partial Rebuild of 138 kV Ckts. 21I, 21G, 21Z, and 81F; Installation of an additional 138 kV circuit on existing double-circuit structures | 2004-10-28 | 2005-05-21 |  | 5065000 | 4600000 |  |  | 30% | 138 | NA | 22.5 | 2-959.6 ACSS | Steel Towers, Steel Poles, Concrete Poles, and Wood Poles | 80-255 | 11.6 | NA | NA | 25.101(c)(5)(B) and 25.83(a)(3) |  | 4600000 | 0 | 4600000 |  |  | 4600000 | 0 | 0
510 | Goodyear | Houston, Harris | 138 kV service to customer-owned GDYEAR substation within one mile of Ckt. 70B | 2005-01-10 | 2005-04-01 |  | 570000 | 662000 |  |  | 8% | 138 | NA | 0.28 | 2-959.6 ACSS | Steel Towers, Concrete Poles | NA | NA | 55-125 | 0.14 | 25.101(c)(5)(A) | Actual Cost to be reimbursed by Goodyear. | 662000 | 0 | 662000 |  |  | 662000 | 0 | 0
572 | Sims Bayou | Houston, Harris | Alteration of 138 kV Ckt. 26A as requested by Harris County Flood Control District for bayou widening | 2004-12-20 | 2005-02-28 |  | 495000 | 495000 |  |  | 95% | 138 | NA | 0.7 | 397 ACSR | Steel Towers | 50 | 0.7 | NA | NA | 25.101(c)(5)(F) | Actual cost to be reimbursed by Harris County Flood Control District. | 495000 | 0 | 495000 |  |  | 495000 | 0 | 0
594 | Texas Southern University | Houston, Harris | Relocation of 69 kV Ckt. 46A and 138 kV Ckt. 37C to avoid an encroachment by the TSU parking garage | 2005-02-15 | 2005-03-20 |  | 1000000 | 1000000 |  |  | 0% | 138 | NA | 0.42 | 795 AAC, 2000 AAC | Steel Poles | Substation Property | 0.05 | Street, 10-32 | 0.21 | 25.101(c)(5)(E) | Actual cost to be reimbursed by TSU. | 1000000 | 0 | 1000000 |  |  | 1000000 | 0 | 0
351 | Trinity Bay Substation | Baytown, Chambers | 138 kV Service to Trinity Bay Substation within one mile of Ckt. 03B | 2004-12-01 | 2005-03-04 |  | 211000 | 211000 |  |  | 92% | 138 | NA | 0.1 | 2-795 ACSR | Steel Towers, Concrete Poles | Substation Property | 0.05 | NA | NA | 25.101(c)(5)(A) |  | 211000 | 0 | 211000 |  |  | 211000 | 0 | 0
392 | Obrien - Flewellen | Fort Bend | Reconductor and Partial Rebuild of 138 kV Ckt. 73D | 2005-01-18 | 2005-06-01 |  | 1450000 | 1296000 |  |  | 2% | 138 | NA | 6.6 | 2-959.6 ACSS | Steel Towers, Wooden H-Frames | 100-300 | 6.6 | NA | NA | 25.101(c)(5)(B) |  | 1296000 | 0 | 1296000 |  |  | 1296000 | 0 | 0
528 | Central Street | Houston, Harris | Alteration of 69 kV Ckt. 55C as requested by City of Houston for road widening | 2005-07-15 | 2005-10-01 |  | 214000 |  |  |  | 0% | 69 | NA | 0.2 | 2000 AAC | Steel Towers, Concrete Poles | 75 | 0.2 | NA | NA | 25.101(c)(5)(F) | Actual cost to be reimbursed by City of Houston. | 214000 | 0 | 214000 |  |  | 214000 | 0 | 0
596 | Cedar Bayou - Baytown | Baytown, Chambers, Harris | Partial Reconductor and Partial Rebuild of 138 kV Ckt. 88A | 2005-02-01 | 2005-04-15 |  | 1000000 | 1205000 |  |  | 5% | 138 | NA | 4.1 | 2-959.6 ACSS | Steel Towers | 65-110 | 4.1 | NA | NA | 25.101(c)(5)(B) |  | 1205000 | 0 | 1205000 |  |  | 1000000 | 205000 | 205000
273 | King 35 kV Substation | Harris | 138 kV Service to King 35 kV Substation within one mile of Ckts. 94A and 94B | 2005-04-15 | 2005-06-01 |  | 250000 |  |  |  | 0% | 138 | NA | 0.6 | 795 AAC | Concrete Poles, Steel Towers | Substation Property, 187 | 0.6 | NA | NA | 25.101(c)(5)(A) |  | 250000 | 0 | 250000 |  |  | 250000 | 0 | 205000
406 | Glenwood - Greens Bayou | Houston, Harris | Partial Reconductor and Partial Rebuild of 138 kV Ckt. 95C | 2005-03-28 | 2005-06-01 |  | 866000 |  |  |  | 0% | 138 | NA | 1.6 | 2-959.6 ACSS | Concrete Poles | Street | 1.6 | NA | NA | 25.101(c)(5)(B) |  | 866000 | 0 | 866000 |  |  | 866000 | 0 | 205000
454 | Grant - Plaza | Houston, Harris | Partial Rebuild of 138 kV Ckt. 08I | 2005-04-01 | 2005-06-01 |  | 300000 |  |  |  | 0% | 138 | NA | 1.7 | 2000 AAC | Concrete Poles | Street | 1.7 | NA | NA | 25.101(c)(5)(B) |  | 300000 | 0 | 300000 |  |  | 300000 | 0 | 205000
547 | Freeport LNG (QNTANA) | Freeport, Quintana, Brazoria | 69 kV Service to Customer-owned QNTANA Substation from Ckt. 47B | 2006-07-14 | 2006-11-30 |  | 6395000 |  |  |  | 0% | 69 | NA | 7.8 | 1433.6 ACSS | Concrete Poles, Steel Poles, Steel Towers | NA | NA | 50-100 | 3.9 | Docket No. 30617 | New Project. CCN Filed 1/28/05. | 6395000 | 0 | 6395000 |  |  | #N/A | #N/A | #N/A
585 | Avenue P | Deer Park, Harris | Alteration of 138 kV Ckt. 06B as requested by City of Deer Park for road construction | 2005-04-01 | 2005-04-07 |  | 26000 |  |  |  | 0% | 138 | NA | 0.2 | 2-795 AAC | Steel Pole, Wooden H-Frames | 150 | 0.2 | NA | NA | 25.101(c)(5)(F) | New Project. Actual cost to be reimbursed by City of Deer Park. | 26000 | 0 | 26000 |  |  | #N/A | #N/A | #N/A
597 | Addicks Substation | Houston, Harris | 138 kV Service to Addicks Substation within one mile of Ckt. 24A | 2005-05-15 | 2005-06-01 |  | 155000 |  |  |  | 0% | 138 | NA | 0.2 | 795 ACSR | Steel Towers, Concrete Pole | Substation Property, 300 | 0.2 | NA | NA | 25.101(c)(5)(A) | New Project. | 155000 | 0 | 155000 |  |  | #N/A | #N/A | #N/A
608 | Mary's Creek Substation | Pearland, Brazoria | 138 kV Service to Mary's Creek Substation within one mile of Ckt. 06K | 2005-04-15 | 2005-05-01 |  | 40000 |  |  |  | 0% | 138 | NA | 0.1 | 795 AAC | Steel Towers, Concrete Pole | Substation Property, 80 | 0.05 | NA | NA | 25.101(c)(5)(A) | New Project. | 40000 | 0 | 40000 |  |  | #N/A | #N/A | #N/A
615 | Gable Street - Garden Villas | Houston, Harris | Minor alteration of 69 kV Ckt. 46A due to expiration of temporary easement | 2005-05-01 | 2005-06-01 |  | 255000 |  |  |  | 0% | 69 | NA | 0.16 | 795 ACSR | Concrete Poles, Steel Towers | Street | 0.12 | 11-15 | 0.04 | 25.83(a)(3) | New Project. | 255000 | 0 | 255000 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
|  |  | 6871000 | [19 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[8 empty] | 0 | [14 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 7268545 | 8334000 | 82218000 | 90552000
[24 empty] | 3 | 24 | 27 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## EGSI
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
CEA TL3429 | Line 820 - 138 kV Transmission line between Conroe Bulk and Forest Substations | Montgomery County | Construct a 138 kV Transmission Line 820 from Conroe Bulk to the site of the new Forest Substation to support load growth in Montgomery County, Texas | 2002-02-01 | 2002-06-01 |  | 3837000 |  |  |  | 100% |  | 138 | 5.6 | 666 ACSR Bundled | Concrete or Steel Single Pole Structures |  |  | 80 | 5.6 | PUCT Docket No. 23429 | We are working on the final cost. | 3837000 | 0 | 3837000 |  |  | 3837000 | 0 | 0
TL-3622 | Kinder-Morgan - Copeland Switch Station Line-571 Tap | Montgomery County, TX | Cut Line 571 into and out of new Copeland Switchyard | 2002-10-02 | 2003-04-09 |  | 401888 |  | 326985 | 19% | 100% | 138 |  | 0.21 | 666 ACSR Bundled | 5 Concrete Poles | 100 | 0.1 |  |  | §25.101(c)(2)(C)(i) | Project was cancelled before completion due to floodplain issues. | 401888 | 401888 | 0 |  |  | 401888 | 0 | 0
TL3560 | L-822 China to Porter 230KV Line | Jefferson, Liberty, Harris and Montgomery Counties | Construct 230KV single pole line from China Substation to the new proposed Porter Substation | 2004-04-01 | 2005-05-01 |  | 26953590 |  |  |  | 35% |  | 230 | 65 | 954 ACSR | Concrete or Steel Poles | 212 | 65 |  |  | Docket No. 27145 | Construction has begun on both ends of the line. | 26953590 | 0 | 26953590 |  |  | 26953590 | 0 | 0
TL3602 | L-6 Amelia to Sour Lake Rebuild a section of line | Hardin County | Replace 65 Structures and reconductor 8.4 Miles of 2/0 CU w/ 666 ACSR. | 2003-07-15 | 2004-05-28 | 2004-05-28 | 1713311 |  |  |  | 100% | 69 |  | 8.4 | 666 ACSR | 65 Concrete |  | 8.4 |  |  | 25.101(c)(5)(B)(i) | Working on finalizing costs | 1713311 | 0 | 1713311 |  |  | 1713311 | 0 | 0
TL4421 | NGPL (Kinder Morgan) to Devers 138 kV Line | Liberty County | Build a 4 mile long 138 kV Transmission Line which will tie into existing L-424 and will provide a dual feed into the new Devers Marsh Switchyard | 2004-01-05 | 2004-04-30 | 2004-07-07 | 2333000 |  |  |  | 100% |  | 138 | 8 | 1272 ACSR (Bittern) | Concrete or Steel |  |  | 100 | 4 | Docket No. 27607 | Working on finalizing costs | 2333000 | 0 | 2333000 |  |  | 2333000 | 0 | 0
TL4398 | L-828 Rebuild and Reconductor | Jefferson County, TX | Rebuild & reconductor 138kV L-828 from Str. 12 to Str. 34. Relocate a section inside the ExxonMobil Refinery to make room for the cut-in of L-457 into Carroll Street Park Sub. | 2004-02-01 | 2005-01-14 | 2005-01-14 | 1025857 |  |  |  | 100% | 138 |  | 1.25 | 1590ACSR | 23 Concrete and Steel Poles | 50 | 0.3 | 50 | 0.95 | 25.101(c)(5)(B)(i) and 25.101(c)(5)(D)(i)(ii) | This project involves two Phases. Phase I will start 2-1-04 and Phase II will start 11-1-04. All new R/W is entirely on ExxonMobil property. | 1025857 | 0 | 1025857 |  |  | 1025857 | 0 | 0
GS0148 | Dayton-Gordon Construct New 138kV transmission line. | Liberty County, TX | Construct new 138kV single pole single circuit transmission line for Coastal Water Authority to their Trinity River Pumping Station | 2005-12-15 |  |  | 10370000 | [5 empty] | 138 | 11.4 | 666ACSR | Concrete and Steel Poles |  |  | 100 | 11.4 | Docket No. 28938 | R/W acquisition has begun. | 10370000 | 0 | 10370000 |  |  | 10370000 | 0 | 0
TL4397 | Cut 138kV L-457 into and out of Carroll Street Park Switching Station | Jefferson County | Construct 1.57 miles of single pole double circuit 138kV transmission line from existing L-457 to Carroll Street Park Switching Station for ExxonMobil. This project is entirely on ExxonMobil property. | 2004-05-03 |  |  | 1700000 |  |  |  | 100% | 138 |  | 3.14 | 1590ACSR | 35 Concrete & Steel Poles |  |  | 80 | 1.57 | Docket No. 29079 | Working on finalizing costs. | 1700000 | 0 | 1700000 |  |  | 1700000 | 0 | 0
TL4433 | Johnstown-Porter Construct New 230kV Transmission Line | Montgomery County, TX | Construct 4.9 miles of single pole double circuit designed 230kV transmission line from Porter Substation to the new Johnstown Substation | 2005-12-01 |  |  | 5332055 | [5 empty] | 230 | 9.8 | Bundled 954 ACSR | Concrete or Steel |  |  | 100 | 4.9 | Docket No. 29420 | Entergy is currently in negotiations with the intervenors in this case for a settlement agreement. | 5332055 | 0 | 5332055 |  |  | 5332055 | 0 | 0
TL4439 | L-88 Rebuild W/L-599 | Jefferson County, TX | Rebuild L-88 double circuit w/L-599 from Fontenot's Corner to Beaver's Corner | 2004-07-15 |  |  | 1969338 |  |  |  | 25% | 138 |  | 9 | Bundled 666 ACSR |  |  |  | 175 | 9 | 25.101(c)(5)(B)(i)(ii) and 25.101(c)(5)(C)(i)(ii) | This project is for installation of conductor only. The poles are covered under the L-599 rebuild project number TL4377. | 1969338 | 0 | 1969338 |  |  | 1969338 | 0 | 0
TL4377 | L-599 Rebuild Amelia to China | Jefferson County, TX | Rebuild L-599 from Amelia Sub to China Bulk double circuit w/138kV L-88 | 2004-07-15 |  |  | 2855540 |  |  |  | 65% | 230 |  | 17.32 | Bundled 954 ACSR | 156 Structures Concrete & Steel Poles |  |  | 175 | 17.32 | 25.101(c)(5)(B)(i)(ii) | 9 Miles of this rebuild will be double circuit with 138 kV L-88 which is being done under CEA # TL4439 | 2855540 | 0 | 2855540 |  |  | 2855540 | 0 | 0
TL4437 | L-424 Double Circuit W/L-496 | Jefferson County,TX | Rebuild L-424 Double Circuit W/L-496 from China Bulk to Beavers Corner (2.8 miles) | 2004-07-15 |  |  | 333503 |  |  |  | 55% | 138 |  | 2.8 | 954 ACSR |  |  |  | 500 | 2.8 | 25.101(c)(5)(B)(i)(ii) and 25.101(c)(5)(C)(i)(ii) | This project is for installation of conductor only. The poles are covered under the L-496 rebuild project number TL4435. | 333503 | 0 | 333503 |  |  | 333503 | 0 | 0
TL4435 | L-496 Double Circuit W/L-424 | Jefferson County, TX | Rebuild L-496 Double Circuit W/L-424 from China Bulk to Beavers Corner (2.8 miles) | 2004-07-15 |  |  | 1385501 |  |  |  | 55% | 230 |  | 2.8 | Bundled 954 ACSR | 28 Concrete Poles |  |  | 500 | 2.8 | 25.101(c)(5)(B)(i)(ii) | This project is in conjunction with the L-424 rebuild under CEA number TL4437. This line and L-424 are existing in the same R/W and are being rebuilt and double circuited to clean-up the R/W. | 1385501 | 0 | 1385501 |  |  | 1385501 | 0 | 0
TL4418 | L-86 Rebuild W/L-822 | Liberty County, TX | Rebuild L-86 double circuit W/new L-822 for 3.0 Miles in existing R/W |  |  |  | 927361 |  |  |  |  | 138 |  | 3 | 954 ACSR |  |  |  | 175 | 3 | 25.101(c)(5)(C)(i)(ii) | This 3.0 mile section of 138kV L-86 is being rebuilt with new L-822 to clean-up the R/W and upgrade the conductor. | 927361 | 0 | 927361 |  |  | 927361 | 0 | 0
GS0235 | Louisiana Pacific, Silsbee 69kV POD | Hardin County, TX | Install 3 way GOAB switch and .2 mile radial 69kV L-471 to new customer owner Substation | 2004-11-22 |  |  | 380213 |  |  |  |  | 69 |  |  | 666ACSR | 4 Concrete |  |  | 60 | 0.2 | 25.101(c)(5)(A)(i)(ii) | This project is entirely on property owned by Louisiana Pacific | 380213 | 0 | 380213 |  |  | 380213 | 0 | 0
TL4523 | L-552 cut-in to New Memorial Substation | Jefferson County, TX | Install 7 structures to cut L-552 into and out of New Memorial Substation | 2004-12-15 | 2005-01-05 | 2005-01-05 | 312048 |  |  |  | 100% | 138 |  | 0.32 | Bundled 395 ACAR | 7 concrete |  |  |  |  | §25.101(c)(2)(C)(i) | This project is to cut 138kV line 552 into the new Memorial Substaiton. There is no R/W because the substation is adjacent to the transmission R/W | 312048 | 0 | 312048 |  |  | 312048 | 0 | 0
GS0223 | Memorial Herrman Hospital-Relocate 1250Ft. Of L-169 | Montgomery County, TX | This project is to replace approximately 1250 ft. of 138kV Line 169 with underground cable. This relocation is to allow for expansion of the hospital and parking lot. | 2005-02-01 |  |  | 2150000 |  |  |  |  | 138 |  | 0.23 | 4933kcmil | Underground | 80 | 0.23 |  |  | 25.101(c)(5)(D)(i)(ii) and 25.101(c)(5)(E) | Memorial Herrman Hospital has requested Entergy to place approximately 1250 ft. of 138kV Line 169 underground to allow for expansion of their facility and to increase the size of their parking lot. They did not want the line overhead over the new parking lot and requested that we put the line underground. The relocation is entirely on their property and within existing R/W. The new agreement will decrease the R/W from 80' wide to 30' wide. | 2150000 | 0 | 2150000 |  |  | 2150000 | 0 | 0
TL4399 | Carroll Street Park-South Beaumont Reconductor L-465 & L-828 | Jefferson County, TX | Reconductor L-465 & L-828 from marsh area coming out of ExxonMobil plant to South Beaumont Substation. L-465 is an old section of L-457 that was renumbered. | 2005-02-15 |  |  | 1834000 |  |  |  | 20% | 138 |  | 2.01 | 1590 ACSR | 7-Steel Double Circuit; 1 Steel Single Circuit; 10 Concrete Double Circuit; 2 Concrete Single Circuit | 150 | 2.01 |  |  | 25.101(c)(5)(B)(i)(ii) | This project is part of the optional upgrades accociated with the ExxonMobil co-generation project. | 1834000 | 0 | 1834000 |  |  | 1834000 | 0 | 0
TL4398 STAFF A | Rebuild the section of L-828 from the Railroad Tracks to Carroll Street Park Substation | Jefferson County, TX | Rebuild and reconductor the section of L-828 between structures 7 and 14. | 2005-02-15 |  |  | 406000 |  |  |  |  | 138 |  | 0.5 | 1590 ACSR | 2 Steel Poles & 7 Concrete Poles | 0 | 0.5 |  |  | 25.101(c)(5)(B)(i)(ii) | The work on this section of L-828 could not completed until L-457 was routed into Carroll Street Park substation. Please note that the reported R/W width is "0" because the line in the street R/W by virtue of the franchise agreement. | 406000 | 0 | 406000 |  |  | 406000 | 0 | 0
TL4438 | L-88 Rebuild section with L-822 | Jefferson & Hardin County, TX | Rebuild Existing 138kV L-88 double circuit with new 230kV L-822 from China Substation to Dayton Bulk Substation | 2005-03-05 |  |  | 4173998 | 4534146 |  |  |  | 138 |  | 31.1 | Bundled 666 ACSR |  | 212 | 31.7 |  |  | 25.101(c)(5)(B)(i)(ii) | L-88 is an existing 138kV line which is being rebuilt on the second circuit position of new 230kV L-822. | 4534146 | 0 | 4534146 |  |  | #N/A | #N/A | #N/A
TL4417 | L-571 Reroute at Porter Substation | Montgomery County, TX | Reroute 138kV L-571 from Tamina Substation to Porter Substation | 2005-03-15 |  |  | 222173 | 252320 |  |  |  | 138 |  | 0.27 | Bundled 666 ACSR | 3 Steel Poles |  |  |  |  | 25.101(c)(5)(A)(i)(ii) | All work is on Entergy property. No new R/W was required. | 252320 | 0 | 252320 |  |  | #N/A | #N/A | #N/A
TL4434 | L-586 Reroute at Porter Substation | Montgomery County, TX | Reroute 138kV L-586 from Tamina Substation to Porter Substation | 2005-03-20 |  |  | 215685 | 238410 |  |  |  | 138 |  | 0.26 | 954 ACSR | 3 Steel Poles |  |  |  |  | 25.101(c)(5)(A)(i)(ii) | All work is on Entergy property. No new R/W was required. | 238410 | 0 | 238410 |  |  | #N/A | #N/A | #N/A
TL4441 | L-826 Reroute at Porter Substation | Montgomery county, TX | Reroute 138kV L-826 from Tamina Substation to Porter Substation | 2005-03-20 |  |  | 131370 | 218495 |  |  |  | 138 |  | 0.26 | 954 ACSR | 3 Steel Poles |  |  |  |  | 25.101(c)(5)(A)(i)(ii) | All work is on Entergy property. No new R/W was required. | 218495 | 0 | 218495 |  |  | #N/A | #N/A | #N/A
TL4442 | L-582 Reroute at Porter Substation | Montgomery county, TX | Reroute 138kV L-582 from Tamina Substation to Porter Substation | 2005-03-25 |  |  | 374100 | 393287 |  |  |  | 138 |  | 0.5 | Bundled 666 ACSR | 6 Steel Poles |  |  |  |  | 25.101(c)(5)(A)(i)(ii) | All work is on Entergy property. No new R/W was required. | 393287 | 0 | 393287 |  |  | #N/A | #N/A | #N/A
TL4419 | L-823 Build Extension from Porter Substation to Tamina Substation | Montgomery County, TX | Construct 138kV L-823 from Porter Substation to Tamina Substation | 2005-03-25 |  |  | 373772 | 493497 |  |  |  |  | 138 | 0.5 | Bundled 666 ACSR | 6 Steel Poles |  |  |  |  | 25.101(c)(5)(A)(i)(ii) | All work is on Entergy property. No new R/W was required. | 493497 | 0 | 493497 |  |  | #N/A | #N/A | #N/A
TL4398 STAFF B | L-86 Rebuild W/L-822 from Kinder Morgan Tap to Porter Substation | Montgomery County, TX | L-86 rebuild on the second circuit position of new L-822 | 2005-03-25 |  |  | 1148087 | 775977 |  |  |  | 138 |  | 2 | 954 ACSR | [5 empty] | 25.101(c)(5)(B)(i)(ii) | This is conductor work only. The structures are captured under the work for L-822 (TL3560). | 775977 | 0 | 775977 |  |  | #N/A | #N/A | #N/A
6906132
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 326985 | 401888 | 72724449 | 73126337
[24 empty] | 1 | 25 | 26 | Project Count
[24 empty] | Completed | Active | Total
Note on A20: Allen Steven Boling: STAFF MODIFIED PROJECT NUMBER TO CREATE A UNIQUE PROJEC NUMBER.
Note on A27: Allen Steven Boling: STAFF REVISED PROJECT NUMBER TO CREATE A UNIQUE PROJECT. TL4418 USED IN A DIFFERENT PART OF THIS PROJECT.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## EPE
[13 empty] | RIGHT OF WAY | [9 empty] | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS
EPE PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS | COMPLETED PROJECTS | ACTIVE PROJECTS | DATE APPROVED | REQUESTED ADDITIONAL INFORMATION | VAR. (%) | VAR. (%) | 0
1240 | Montwood to Coyote 115kV Line (12600 Line) | El Paso County | As a part of the overall Eastside Expansion Plan, a new line is to be constructed between Montwood and Coyote Substations. The new line will be constructed utilizing single pole steel structures. The preferred route is approximately 7.8 miles in length. | 2002-04-01 | 2005-09-30 | 2689462.61 |  |  |  | 7.84 Miles | 954 ACSR | 90' galvanized steel single pole structures. | 120' platted road rights of way | 0.29 miles | 100', 10 to15' | 2.94 mile, 4.61mi. (overhang) | 24666 | Right of Way acquisition complete. Work Orders to be updated and materials ordered. Construction scheduled to begin in 2005 |  | 2689462.61 |  |  |  | 0
1161 | Santa Teresa - Montoya 115 kV Line | El Paso County & Dona Ana County, New Mexico | Construct approximately 7.19 miles of 115kV transmission line on single pole structures to complete an electrical loop between Santa Teresa Substation (Dona Ana County, NM.) and Montoya Substation (El Paso County, TX). The project is intended to improve service reliability and provide for future electrical load growth in the project area. | 2006-01-11 | 2006-06-30 | 5774930 |  |  |  | 7.19 miles | 954 ACSR | 95' galvanized steel single pole structures. | various platted road rights of way adjacent to proposed centerline | 2.29 miles | 25', 50', 100' | 2.29 miles, 4.76 miles, 0.14 mile | 26670 |  |  | 5774930 |  |  |  | 0
1133 | Rio Grande - Sunset 5500/5600 Line Rebuild | El Paso County | A significant portion of these lines currently traverse an active quarry area. EPE and the property owner have discussed the possibility of relocating lines through this property, but it will be some time before the preferred location is suitable for placing permanent structures. In the meantime, EPE will replace wood structures with steel structures at critical points along the existing line route. Replacement of structures has been delayed until 2005 | 2005-05-30 | 2005-07-30 | 436000 |  |  |  | 5500 Line 4.78 miles | 4/0 Copper | 65' to 95' galvanized steel structures. Some will be replacement H-Frame structures, others will be replaced with monopole structures. | 50' | 4.78 miles | N/A | N/A | 25.101(c)(5)(B) | Awaiting material delivery. |  | 436000 |  |  | 0 | 0 | 0
[10 empty] | 5600 Line 5.32 miles | 4/0 Copper |  | 50' | 5.32 miles | N/A | N/A |  |  |  | 0 |  |  | 0 | 0 | 0
1279 | Ascarate - Sunset North 19500 Line Rebuild | El Paso County | Replace existing wood structures with steel monopole structures. | 2004-10-11 | 2005-07-01 | 614000 |  |  | 95% | 7.98 miles | 556 ACSR | Existing single pole wood structures range from 65' to 75' in height. Structures will be replaced with 85' to 95' steel single pole structures. | Varies. Majority of line built in and along dedicated streets and alleys. Overhang and crossing permits previously obtained for original line construction. | 7.98 miles |  |  | 25.101(c)(5)(B) | Job has been modified to replace 2 guyed corner structures with self supporting dead-ends. New structures will be delivered in June. Remainder of structure replacements will be completed by end of January 2005. |  | 614000 |  |  | 0 | 0 | 0
[20 empty] | 0 |  |  |  | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[19 empty] | 0 | 9514392.61 | 9514392.61
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## LCRA
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
1001776, 1001840 | Kunitz-Wink | Culberson, Reeves, Loving, Winkler | New 138 kV transmission line from wind plant at Kunitz to TXU Wink Substation | 2006-06-05 | 2006-11-01 |  | 30212829 |  |  |  | 0% |  | 138 | 101.5 | 3x2-795 kcmil ACSR "Drake" | Single Pole & H-frame | na | 0 | 100 - 160 | 101.5 | CCN Docket No. 22762 approved 7/13/01 |  | 30212829 | 0 | 30212829 |  |  | 30212829 | 0 | 0
1002622, 243801W77032 | Macedonia-Hockley TL Addition | Harris, Waller | New 138 kV transmission line and upgrade of an existing line segment from single to double-circuit, connecting the existing Macedonia Substation to a tie with ReliantHL&P near Hockley Substation | 2003-10-13 | 2004-12-15 | 2004-06-14 | 4066464 | 4066464 |  |  | 100% | 138 | 138 | 11.98 | 3x1-959 kcmil ACSS/TW "Suwannee" | Steel and Concrete Single Pole | 60 | 2.78 | 80 | 9.2 | CCN Docket No. 24380 approved 7/5/02 | Final completion delayed by wet conditions. | 4066464 | 0 | 4066464 |  |  | 4066464 | 0 | 0
1003048 | Fort Lancaster/Friend Ranch | Crockett, Pecos, Terrell | New double-circuit capable 138 kV transmission line from Fort Lancaster to Friend Ranch | 2004-08-02 | 2005-06-30 |  | 20189177 | 24899000 |  |  | 65% |  | 138 | 43.37 | 3x2-795 kcmil ACSR "Drake" (second circuit at later date) | Single Pole | na | 0 | 80 | 43.37 | Joint CCN w/AEP-WTU Docket No. 27015 approved 3/21/03 |  | 24899000 | 0 | 24899000 |  |  | 24899000 | 0 | 0
1002908 | Twin Buttes (from Big Lake) Cut-in to Twin Buttes | Tom Green | New double-circuit capable, 138 kV transmission line from Twin Buttes Switching Station to a cut-in point on the Big Lake/SAPS transmission line and route deviation of previously approved Morgran Creek-Twin Buttes-Red Creek-Comanche 345 kV line | 2004-04-02 | 2004-08-10 | 2004-08-20 | 8511520 | 8674000 | 7198241 | -17.01% | 100% |  | 138 | 14.6 | 3x2-795 kcmil ACSR "Drake" (second circuit at later date) | Single Pole Tangents, Multi-pole angles and deadends Lattice towers on route deviation | na | 0 | 80 | 7.3 | Joint CCN w/AEP-WTU Docket No. 27180 approved 9/26/03 | Amount provided in "Final Actual Project Cost" column does not include costs associated with condemnation appeals. The final actual project cost may change pending the outcome of the appeals. | 8674000 | 8674000 | 0 |  |  | 8674000 | 0 | 0
1001709 1004792 1005095 | HiCross-to-Marshall Ford TL Addition T-142 | Travis, City of Austin | Rebuild existing line and reconductor with bundled 795 ACSR and 1433 Merrimac | 2003-03-08 | 2005-06-30 |  | 5790529.4879 | 5790529.4879 |  |  | 70% | 138 | 138 | 16.52 | 795 kcmil ACSR "Drake" | Steel , Lattice Tower, Concrete | 100 | 16.52 | 0 | 0 | 25.101(c)(5)(B) |  | 5790529.4879 | 0 | 5790529.4879 |  |  | 5790529.4879 | 0 | 0
1004229 | N. McCamey-to-McElroy/N. McCamey Cut-In 2nd Ckt Addition | Crane, Upton | Add a second 138-kV circuit to the existing North McCamey to McElroy/North McCamey Cut-In transmission line | 2004-05-15 | 2004-10-22 | 2004-10-22 | 5210242 | 7465540 |  |  | 100% | na | 138 | 25.5 mi | Bundled 795 kcmil ACSR | Single Pole, Steel or Concrete | Varies, CL - 80 | 25.5 mi | 80 | 0 | CCN Docket No. 27762 | Amending certain easements to 80-ft width | 7465540 | 0 | 7465540 |  |  | 7465540 | 0 | 0
1005023 | Hallettsville-Yoakum City Overhaul T140 | Lavaca, DeWitt | Transmission Line Overhaul | 2003-11-17 | 2005-04-02 |  | 416424 | 416424 |  |  | 97% | 138 | 138 | 9.67 | 336 kcmil ACSR | H-frame, Wood | 100 | 16.02 | 100 | 0 | 25.101(C)(3) | Outage constraints have moved project completion to January 2005. | 416424 | 0 | 416424 |  |  | 416424 | 0 | 0
1005027 | Lampasas-Copperas Cove Overhaul T154 | Lampasas | Transmission Line Overhaul | 2004-04-05 | 2005-05-27 |  | 271085 | 271085 |  |  | 80% | 138 | 138 | 9.67 | 795 kcmil ACSR | H-frame, Wood | 100 | 14.6 | 100 | 0 | 25.101(C)(3) |  | 271085 | 0 | 271085 |  |  | 271085 | 0 | 0
241201W76922 | Glasscock-to-Andice TL Add T413 | Williamson | Add a new 138 kV transmission line from the Glasscock substation to the Andice substation | 2005-10-19 | 2006-06-30 |  | 7459000 |  |  |  | 0% | N/A | 138 | 13.3 | 795 ACSR | single pole, steel or concrete | N/A | N/A | 80 | 13.3 | CCN Docket No. 28450 approved 2/11/05 |  | 7459000 | 0 | 7459000 |  |  | 7459000 | 0 | 0
1003552 1003553 | Kendall-to-CPS Cagnon Road Transmission Line Addition | Kendall | New 345/138 kV from CPS Cagnon Tie Point at the Kendall/Bexar county line to the Kendall Substation | 2005-06-01 | 2006-06-30 |  | 28856400 |  |  |  | 0% |  | 345 | 20 | 1590 kcmil 54/19 "Falcon | Tubular Steel Structures | 100 | 20.4 | 110-150 | 20.4 | CCN Docket No. 29065 - filed 1/30/04 | The proposed route takes advantage of existing 100 foot wide right-of-way for its entire length. However, the new facilities will require that the existing right-of-way be widened an additional 10 to 50 feet depending on the length of the span between structures. | 28856400 | 0 | 28856400 |  |  | 28856400 | 0 | 0
1005107 | Alcoa Sim Gideon - Elgin TL Reloc | Bastrop | Relocate circuit T260 Sim Gideon-Elgin, between structures 7/6 and 9/5, at expense of and on ROW provided by requesting party. This will accommodate the landowner's (Alcoa's) Three Oaks Mine project and involves the removal of 1.78 miles of existing line. | 2004-05-17 | 2004-09-17 | 2004-09-17 | 865310 | 865310 |  |  | 100% | 138 | 138 | 2.35 | 795 ACSR DRAKE | Wood H-frame Tangents, 3-Pole Steel Deadend, 3-Pole Guyed Wood Deadend & Angle | na | 0 | 80 | 2.35 | 25.101(C)(5)(D) |  | 865310 | 0 | 865310 |  |  | 865310 | 0 | 0
1005012 | Yoakum-to-Flatonia TL Reloc | DeWitt, City of Yoakum | Relocate an existing transmission line segment (LCRA TSC Circuit T134), due to requirements of the City of Yoakum and Yoakum ISD | 2004-07-19 | 2004-11-05 | 2004-11-05 | 409000 | 496200 |  |  | 100% | 69 | 69 | 0.29 | 3x1-336 ACSR "Linnet" | Single Pole, Steel | CL | 0.19 | 60 | 0.29 | 25.101(C)(5)(F) |  | 496200 | 0 | 496200 |  |  | 496200 | 0 | 0
1003855 | SH 130 McNeil-to-Cedar Hill TL T146 | Travis | Alter an existing 138 transmission line, LCRA TSC Circuit T146 McNeil-CedarHIll, due to the requirements of govermental body, to accommodate construction of State Highway 130. | 2004-07-09 | 2004-10-30 | 2004-08-18 | 379790 | 379790 |  |  | 100% | 138 | 138 | 0.31 | 3x1-795 ACSR "Drake" | Single Pole, Steel and Prestressed Concrete | 100 | 0.31 | na | 0 | 25.101(C)(5)(F) | No new ROW required | 379790 | 0 | 379790 |  |  | 379790 | 0 | 0
1005925 | Hill Country Transmission Line Project (Cico-to-Helotes TL Addition T-244) | Kendall, Bexar, City of Boerne | Construct a new bundled 795 ACSR 138 kV transmission line approximately 4 miles in length from a tap point on the Boerne Cico-to-Helotes transmission line to the proposed Hill Country Substation. | 2006-01-02 | 2006-05-31 |  | 4551900 |  |  |  | 0% | na | 138 | 3.8 | Bundled 795 kcmil ACSR "DRAKE" | Single Pole, Steel or Prestressed Concrete | na | 0 | 80 | 3.8 | CCN Docket #29684 filed 5/14/04 |  | 4551900 | 0 | 4551900 |  |  | 4551900 | 0 | 0
1005699 | S.Abilene-to-Eskota TL Tap | Taylor | Extension to a new substation, single circuit line in and out of Taylor Electric Cooperative's Potter Substation Addition. | 2004-09-01 | 2004-09-29 | 2004-10-01 | 378560 | 378560 |  |  | 100% | 138 | 138 | 0.068182 | 795 kcmil ACSR "Drake" | Single pole, steel or prestressed concretete | 80 | n/a | 80 | 0.07 | 25.101(C)(5)(A) | New sub cut-in, single circuit in and out of the substation, each span is approximately 160 feet | 378560 | 0 | 378560 |  |  | 378560 | 0 | 0
1004487, 1004488 | Sandy Creek-to-Sunrise Beach TL Addition | Llano | Construction a new 795 ACSR 138 kV transmission line (initially operated at 69 kV) approx. 2.6 miles in length between the new Sandy Creek Substation and the Sunrise Beach Substation. | 2005-12-01 | 2006-06-30 |  | 1934900 |  |  |  | 0% | N/A | 138 | 2.58 | 795 kcmil ACSR "Drake" | Single pole, steel or pre-stressed concrete | N/A | N/A | 80 | 2.58 mi | CCN Docket No. 29833 filed 6/28/04 |  | 1934900 | 0 | 1934900 |  |  | 1934900 | 0 | 0
1006028 | Gonzales-to-Cuero TL T226 Add (Emergency Repairs) | DeWitt | Emergency repair of erosion, installation of sheet piling and security deadend due to emergency conditions created by the Guadalupe River. | 2004-07-20 | 2004-10-30 | 2004-10-30 | 680000 | 680000 |  |  | 100% | 138 | 138 | 0.9 | 3x1-795 ACSR "Drake" | Lattice Tower | 100 | 0.9 | na | 0 | 25.101(C)(3) |  | 680000 | 0 | 680000 |  |  | 680000 | 0 | 0
1004356 | Kendall-Mountain Top TL Add T342 | Kendall, Blanco | Rebuild to increase height of existing structures and operate at higher ampacity, increase line rating, operate at higher temperature | 2004-12-15 | 2005-06-30 |  | 4046186 | 4791000 |  |  | 5% | 138 | 138 | 34.26 | 3x1-336 "Linnet" | H-frame, wood and steel | 100 | 34.26 | na | na | 25.101(C)(5)(B) |  | 4791000 | 0 | 4791000 |  |  | 4791000 | 0 | 0
1004357 | Mountain Top-to-Miller Creek T426 | Blanco, Kendall | Rebuild to increase height of existing structures and operate at higher ampacity, increase line rating, operate at higher temperature | 2005-02-01 | 2005-03-31 |  | 589672 |  |  |  | 0% | 138 | 138 | 35.5 | 3x1 - 336 kcmil ACSR "Linnet" | SC Wood H-Frame | 100 | 35.5 | N/A | N/A | 25.101(C)(5)(B) | An affidavit for the notifications for this project was filed with the July 2004 PUC MCPR. | 589672 | 0 | 589672 |  |  | 589672 | 0 | 0
1006394 | Manor-to-Cedar Hill TL Add T495 | Travis | Extend existing transmission line line into new Manor substation facilities, located within Manor substation properties, from the existing McNeil-Manor-Cedar Hill transmission line. | 2005-02-01 | 2005-02-28 |  | 132268 |  |  |  | 0% | 138 | 138 | 0.09 | 3x2 - 795 kcmil ACSR "Drake" | DC Steel Pole | N/A | N/A | N/A | 0.09 | 25.101(C)(5)(A) | Located on land purchased in fee (substation property) | 132268 | 0 | 132268 |  |  | 132268 | 0 | 0
1006404 | McNeil-to-Manor T146 Add | Travis | Extend existing transmission line line into new Manor substation facilities, located within Manor substation properties, from the existing McNeil-Manor-Cedar Hill transmission line. | 2005-02-01 | 2005-02-28 |  | 132269 |  |  |  | 0% | 138 | 138 | 0.09 | 3x2 - 795 kcmil ACSR "Drake" | DC Steel Pole | N/A | N/A | N/A | 0.09 | 25.101(C)(5)(A) | Located on land purchased in fee (substation property) | 132269 | 0 | 132269 |  |  | 132269 | 0 | 0
1003914 | Bergheim-to-Boerne T238 | Kendall | Construct two TL structures in the Boerne-Fairoaks transmission line to support a 138 kV double circuit transmission line tap to the CPS Fairoaks Ranch Substation. | 2004-11-15 | 2005-03-31 |  | 535848 |  |  |  | 50% | 138 | 138 | 0.19 | 3x1 - 795 kcmil ACSR "Drake" | SC Steel Pole | 100 | 0.19 | N/A | N/A | 25.101(C)(5)(B) | Work started on substation property prior to inclusion on PUC MCPR. | 535848 | 0 | 535848 |  |  | 535848 | 0 | 0
1005067 | Kendall-to-Kerrville T123 TL Add | Kendall | Modify existing line and extend into new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2004-12-06 | 2004-12-23 | 2005-01-14 | 237900 | 237900 |  |  | 100% | 138 | 138 | 0.6 | 3x1 - 795 kcmil ACSR "Drake" | SC Lattice Tower/Concrete Single Pole | N/A | N/A | N/A | 0.6 | 25.101(C)(5)(A) & 25.101(C)(5)(B) | Work started on substation property prior to inclusion on PUC MCPR. | 237900 | 0 | 237900 |  |  | 237900 | 0 | 0
1005075 | Kendall-to-Comfort T243 TL Add | Kendall | Modify existing line and extend into new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2004-12-06 | 2004-12-23 | 2005-01-14 | 501400 | 501400 |  |  | 100% | 138 | 138 | 0.33 | 3x2 - 795 kcmil ACSR "Drake" | SC Lattice Tower/Steel Pole | N/A | N/A | N/A | 0.33 | 25.101(C)(5)(A) & 25.101(C)(5)(B) | Work started on substation property prior to inclusion on PUC MCPR. | 501400 | 0 | 501400 |  |  | 501400 | 0 | 0
1005065 | Kendall-to-Fredericksburg T120 TL Add | Kendall | Modify existing line and extend into new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2005-01-18 | 2005-01-21 | 2005-01-21 | 415903 | 415903 |  |  | 100% | 138 | 138 | 0.31 | 3x1 - 795 kcmil ACSR "Drake" | SC Steel Pole | N/A | N/A | N/A | 0.31 | 25.101(C)(5)(A) & 25.101(C)(5)(B) | On substation property | 415903 | 0 | 415903 |  |  | 415903 | 0 | 0
1005073 | Kendall-to-Mountain Top T342 TL Add | Kendall | Modify existing line and extend into new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2005-01-17 | 2005-01-21 | 2005-02-08 | 221493 | 221493 |  |  | 100% | 138 | 138 | 0.22 | 3x1 - 336 kcmil ACSR "Linnet" | SC Steel Pole | N/A | N/A | N/A | 0.22 | 25.101(C)(5)(A) & 25.101(C)(5)(B) | On substation property | 221493 | 0 | 221493 |  |  | 221493 | 0 | 0
1006222 | Lon Hill-to-Citgo North Oak Park T436 Add | Nueces | Modify existing transmission line and extend into the new Valero Cantwell Substation, located on Valero and Substation properties, from the existing Long Hill-to-Citgo North Oak Park transmission line. | 2005-02-14 | 2005-03-31 |  | 200000 |  |  |  | 0% | 138 | 138 | 0.043561 | 3X2 - 1272 kcmil ACSR | DC Steel Pole | N/A | N/A | 100 | 0.04 | 25.101(C)(5)(A) & 25.101(C)(5)(B) | Split into new Cantwell Substation for Valero. | 200000 | 0 | 200000 |  |  | 200000 | 0 | 0
1006453 | Buchanan-to-CTEC Buchanan T106 TL Add | Llano | Modify existing transmission line andextend into new Coronado Switchyard. | 2005-02-15 | 2005-05-31 |  | 103000 |  |  |  | 0% | 69 | 69 | .1 mi | 3x1 - 336 kcmil ACSR "Linnet" | Lattice Tower | N/A | N/A | 100 | 0.19 | 25.101(C)(5)(A) & 25.101(C)(5)(B) |  | 103000 | 0 | 103000 |  |  | 103000 | 0 | 0 | 0
1006455 | Buchanan-to-Burnet T108 TL Add | Llano | Modify existing transmission line and extend into new Coronado Switchyard. | 2005-02-15 | 2005-05-31 |  | 67000 |  |  |  | 0% | 69 | 69 | 0.04 | 3x1-4/0 ACSR "Penguin" | Wood H-frame | N/A | N/A | 100 | 0.04 | 25.101(C)(5)(A) & 25.101(C)(5)(B) |  | 67000 | 0 | 67000 |  |  | 67000 | 0 | 0
1006457 | Buchanan-to-Fairland T110 TL Add | Llano | Modify existing transmission line and extend into new Coronado Switchyard. | 2005-02-15 | 2005-05-31 |  | 88000 |  |  |  | 0% | 138 | 138 | 0.26705 | 3x1 - 795 kcmil ACSR "Drake" | Lattice Tower | N/A | N/A | 100 | 0.26705 | 25.101(C)(5)(A) & 25.101(C)(5)(B) |  | 88000 | 0 | 88000 |  |  | 88000 | 0 | 0
1006459 | Buchanan-to-Coronado TL Add | Llano | Extend transmission line from Buchanan Sub to new Coronado Switchyard. | 2005-02-15 | 2005-05-31 |  | 163000 |  |  |  | 0% | 69 | 69 | 0.08 | 3x1 - 336 kcmil ACSR "Linnet" | Lattice Tower | N/A | N/A | N/A | 0.08 | 25.101(C)(5)(A) |  | 163000 | 0 | 163000 |  |  | 163000 | 0 | 0
1005069 | Kendall-to-Zorn T389 TL Add | Kendall | Extend existing line to new station facilities--new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2005-04-15 | 2005-05-30 |  | 752000 |  |  |  |  | 345 | 345 | .1 mi | 3x2-795 kcmil ACSR Bundled "Condor" | Single Steel Poles | N/A | N/A | N/A | 0.1 | 25.101(C)(5)(A) | Located on station property | 752000 | 0 | 752000 |  |  | #N/A | #N/A | #N/A
1005071 | Kendall-to-BoerneT228 TL Add | Kendall | Extend existing line to new station facilities--new bay position to accommodate autotransformer addition at Kendall Switchyard. | 2005-05-02 | 2005-05-30 |  | 594000 |  |  |  |  | 138 | 138 | .1 mi | 3x2-795 kcmil ACSR Bundled "Condor" | Single Steel Poles | N/A | N/A | N/A | 0.1 | 25.101(C)(5)(A) | Located on station property | 594000 | 0 | 594000 |  |  | #N/A | #N/A | #N/A
1005595 | Ferguson-to-Horseshoe Bay Fiber Add T193 | Llano | Replace existing shield wire with optical ground wire, add one structure in Horshoe Bay Substation | 2005-04-02 | 2005-05-15 |  | 280000 |  |  |  |  | 138 | 138 | 2.7 | 3x1-795 kcmil ACSR "Drake" | Single Steel Poles | 100-ft | 2.7 | N/A | N/A | 25.101(C)(5)(B) |  | 280000 | 0 | 280000 |  |  | #N/A | #N/A | #N/A
1006169 | Ingram-to-Hunt TL Add | Kerr | Modify existing transmission line to accommodate the addition of circuit breakers at Ingram Substation. | 2005-04-01 | 2005-04-08 |  | 105000 |  |  |  |  | 138 | 138 | 0.1 | 3x1-336 kcmil ACSR "Linnet" | Lattice Tower | 80-ft | 0.1 | N/A | NA | 25.101(C)(5)(A) & 25.101(C)(5)(B) |  | 105000 | 0 | 105000 |  |  | #N/A | #N/A | #N/A
1006292 | Goforth-to-Rohr-to-Canyon TL Sub Add | Hays | Rebuild existing line to accommodate substation construction--add one new steel structure and replace an existing H-frame structure with a steel mono pole. | 2005-04-04 | 2005-05-31 |  | 175000 |  |  |  |  | 138 | 138 | .1 mi | 3x1-336 kcmil ACSR "Linnet" | Single Steel Poles | 100-ft | .1 mi | N/A | N/A | 25.101(C)(5)(A) & 25.101(C)(5)(B) |  | 175000 | 0 | 175000 |  |  | #N/A | #N/A | #N/A
1006398 | HiCross-to-Turnersville TL Add | Travis | Alter and rebuild existing transmission line due to requirements of a govermental body--replace and relocate three tangent structures to accommodate TxDOT SH45SE project. | 2005-04-01 | 2005-04-10 |  | 290000 |  |  |  |  | 138 | 138 | 0.85 | 6x2-795 ACSR kcmil "Drake" | Single Prestressed Concrete Poles | 80-ft | 0.85 | N/A | N/A | 25.101(C)(5)(F) & 25.101(C)(5)(B) |  | 290000 | 0 | 290000 |  |  | #N/A | #N/A | #N/A
1006431 | Bergheim-to-Boerne TL T228 Add | Kendall | Extend existing transmission line into new bay position to accommodate substation construction at Fairoaks Substation. | 2005-04-02 | 2005-04-30 |  | 175000 |  |  |  |  | 138 | 138 | .1 mi | 3x1-795 kcmil ACSR "Drake" | Steel Single Poles | N/A | N/A | N/A | 0.1 | 25.101(C)(5)(A) | Located on station property | 175000 | 0 | 175000 |  |  | #N/A | #N/A | #N/A
1006547 | Coronado T109 Tie-in Add | Llano, Burnet | Rebuild T109 out of Buchanan to accommodate TL tie for the new Coronado Substation. Project includes the removal of three existing structures, the installation of four new structures and conductor upgrade. | 2005-04-02 | 2005-05-31 |  | 1100000 |  |  |  |  | 138 | 138 | 0.42 | 3x1-795 kcmil ACSR "Drake" | Steel Single Poles | N/A | N/A | 80-ft, 100-ft | 0.42 | 25.101(C)(5)(A) |  | 1100000 | 0 | 1100000 |  |  | #N/A | #N/A | #N/A
3471000
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 7198241 | 8674000 | 130373684.4879 | 139047684.4879
[24 empty] | 1 | 38 | 39 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## MVEC
MVEC PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS | COMPLETED PROJECTS | ACTIVE PROJECTS | DATE APPROVED
| Alton 138kV Circuit Tie Line | Hidalgo | 2.4 Miles 138kv Transmission Line | Delayed - March 2005 | Delayed - Estimated October 2005 | 2610000 |  |  | 50% | 2.4 miles | 795 ACSS | Single pole - concrete pole |  |  | 50' | 6336' | 28895 | A temporary tie with AEP was complete on 4-30-05. AEP is building the Key Switching Station estimated to be complete in Oct. 2005. |  | 2610000
| North Edinburg to West Edinburg 138kV Line Rebuild and Second Circuit | Hidalgo | 9.1 Miles 138kv Transmission Line | Delayed- Oct. 2005 | Delayed- Jan. 2006 | 2600000 |  |  | 0% | 9.1 miles | 795 ACSS | Single pole - concrete pole |  |  | 50' | 29040 | 29225 | Currently in design |  | 2600000
1972336 | Kenaf Plant | Willacy | 6.5 Miles 138kv Transmission Line | Delayed - May not be built | Delayed - May not be built | 1550000 |  |  | 0% | 6.5 miles | 795 ACSR | Single pole - concrete pole with steel davit arms |  |  | 25' | 3600' | 19577 | No change during the past month - MVEC has stopped all work related to this line until the Cooperative has assurances that the new load is going to materialize |  | 1550000
| FM 106 Relocation | Cameron | 1.8 Miles 138kv Transmission Line | Delayed-Sept. 2005 | Delayed- Nov. 2005 | 1000000 |  |  | 7% | 1.8 miles | 559 AAAC | Single pole - concrete pole |  |  | 28' | 9468' |  | A temporary relocation for a new bridge widening was performed. |  | 1000000
| West Edinburg to Alton - Reconductor | Hidalgo | 6.5 Miles 138kv Transmission Line | 2005-05-15 | 2005-07-08 | 700000 |  |  | 0% | 6.5 miles | 795 ACSR | Single pole - concrete pole | 28' | 34,320' |  |  |  | TXDOT acquired additional ROW on FM 106 |  | 700000
0
0
0
0
0
0
0
0
0
[19 empty] | 0 | 8460000 | 8460000
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## PEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
XE974659Y | FRIENDSHIP TO MANCHACA | HAYS, TRAVIS COUNTY | CONSTRUCT 138KV FROM FRIENDSHIP TO MANCHACA SUBS, NEW SUBSTATION IN CIRCLE C | UNKNOWN | UNKNOWN |  | 6863881 |  |  |  | 0% | NA | 138 | 7.8 | 795 ACSR DRAKE,SINGLE | SINGLE POLE, STEEL OR CONCRETE | NA | NA | NA | NA | 18389 | 3700 FEET ACROSS CIRCLE C GOLF COURSE WILL BE UNDERGROUND |  | 0 | 0 |  |  | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## SPS
RIGHT OF WAY
SPS PROJECT NUMBER | PROJECT NAME | LOCATION | DESCRIPTION | START DATE | FINISH DATE | ESTIMATED | FINAL | VAR. (%) | % COM | Length | CONDUCTOR | STRUCTURE | W | L | W | L | RULE SECTION AND/OR PUC CONTROL NUMBER | COMMENTS | COMPLETED PROJECTS | ACTIVE PROJECTS | DATE APPROVED | REQUESTED ADDITIONAL INFORMATION
10229735 | Amerada Hess to Doss | Gaines | 5.5 miles of 115 kV transmission line | 2004-07-01 | 2004-12-31 | 850000 | N/A | N/A | 10% | 5.5 miles | 397.5 MCM ACSR | 2-pole wood |  |  | 60ft. | 5.5 miles | Docket No. 28390 |  |  | 850000
| Lubbock East to Crosby | Hale/Floyd | 26.75 miles of 115 kV transmission line | NA |  | 5237158 |  |  | N/A | 26.25 miles | 397.5 MCM ACSR | Single-Shaft Steel | N/A | N/A | 60ft. | 26.25 miles | Docket No. 29391 |  |  | 5237158
| Floyd Tap to Floyd County | Floyd | 6.75 miles of 115 kV transmission line | NA |  | 3832929 |  |  | N/A | 6.75 miles | 397.5 MCM ACSR | Single-Shaft Steel | N/A | N/A | 60ft. | 6.75 miles | Docket No. 29391 |  |  | 3832929
0
0
0
0
123
|  |  | new projects: | 0
[19 empty] | 0 | 9920087 | 9920087
NEW
EXISTING
CONSTRUCTION COSTS
NEW
EXISTING
CONSTRUCTION COSTS

## STEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
700-4257, 700-6259, 700-9258 &800-4256 | Plainview | Wharton | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2001-06-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
700-6267, 700-9266, 700-4265 &800-4264 | Clemville South | Matagorda | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2001-06-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
700-6239, 700-9238, 700-4237 &800-4236 | Charco | Goliad | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2001-06-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Accounting closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
700-9250, 700-6251, 700-4249 &800-4248 | Ganado | Jackson | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2001-06-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Accounting closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
700-4201, 700-9202, 700-6203 &800-4200 | Tilden | McMullen | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2001-06-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Accounting closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
700-6151, 700-4149, 700-9150 &800-4148 | Refugio | Refugio | Install equipment required for substation automation, SCADA & Communications | 2000-08-01 | 2002-12-01 |  | 150000 | 150000 |  |  | 100% | [9 empty] | 25.101 (c) (2) (C ) (i) | Closing out. | 150000 | 0 | 150000 |  |  | 150000 | 0 | 0
702.2057 | Placedo 69 kV Breaker Addition | Victoria | Install 69 kV Breaker on the Vanderbilt line | 2000-12-01 | 2003-04-01 |  | 200000 | 75000 |  |  | 100% | 69 | [8 empty] | 25.101(c) (5)(B)(i) | Accounting closing out. | 75000 | 0 | 75000 |  |  | 75000 | 0 | 0
703.2063 | San Miguel 138 kV Recond. | Atascosa | Reconductor #795 to #1590 Kcmil 138 kV segment. | 2003-09-01 |  |  | 143000 | 143000 |  |  | 100% | 138 |  |  | 1-1590 ACSR | H Frame | 100 | 0.44 |  |  | 25.101(c) (5)(B)(i) | Clean up in process. | 143000 | 0 | 143000 |  |  | 143000 | 0 | 0
703.2068, 803.2067 | Bay City to Sargent 69kV Double Arming | Matagorda | Double arming of a portion of the 69 kV system. | 2003-05-01 | 2003-07-01 |  | 387000 | 387000 |  |  | 100% | 69 |  |  | #4/0 ACSR | Single pole | 50 | 18.5 |  |  | 25.101(c) (5)(B)(i) | Completed. Waiting on accounting. | 387000 | 0 | 387000 |  |  | 387000 | 0 | 0
703.2070,0803.2069 | Vanderbilt to Danevang 138kV Re-insulate | Jackson & Wharton | Replace insulators on a portion of the 138 kV system. | 2003-03-01 | 2003-05-01 |  | 251000 | 251000 |  |  | 100% | 138 |  |  | #477 ACSR | H Frame | 100 | 33.09 |  |  | 25.101 (c) (5) (B)(i) | Completed. Waiting on accounting. | 251000 | 0 | 251000 |  |  | 251000 | 0 | 0
799.1093, 799-2089, 799.4091, 899-2088, 899-1092 899-4090 &799.2087 | Port O'Connor | Calhoun | Expand existing substation | 1999-10-01 |  |  | 850000 | 850000 |  |  | 90% | [9 empty] | 25.101 (c) (2) (C ) (ii) | Rain delay on breaker installations. | 850000 | 0 | 850000 |  |  | 850000 | 0 | 0
702.2103 & 802.2102 | Mathis | San Patricio | Install 2 69 kV Breakers, Panels, and Comm. | 2001-06-01 |  |  | 400000 | 400000 |  |  | 90% | [9 empty] | 25.101(c) (5)(B)(i) | Panels completed. | 400000 | 0 | 400000 |  |  | 400000 | 0 | 0
700.2393 | Nursery Breakers | Victoria | Install 2 69 kV Breakers and Comm. | 2000-12-01 |  |  | 400000 | 400000 |  |  | 45% | [9 empty] | 25.101(c) (5)(B)(i) | Panels on order. | 400000 | 0 | 400000 |  |  | 400000 | 0 | 0
700.2402 | Inez Breakers | Victoria | Install 2 69 kV Breakers and Comm. | 2000-12-01 |  |  | 400000 | 400000 |  |  | 45% | [9 empty] | 25.101(c) (5)(B)(i) | Panels on order. | 400000 | 0 | 400000 |  |  | 400000 | 0 | 0
704.4010, 804.4039, 704.2041, 803.2280 | Poteet Transformer Upgrade | Atascosa | Install 12/16/20 MVA and remove7.5 MVA Transformer | 2004-09-01 | 2005-01-01 |  | 335000 | 335000 |  |  | 75% | 69 | [8 empty] | 25.101 (c) (5) (A) | High siide peers installed. Mobile to be energized this month for pad work. | 335000 | 0 | 335000 |  |  | 335000 | 0 | 0
704.2052 | Industrial Park Breakers | Wharton | Install 2-69 kV Breakers | 2004-10-01 | 2005-02-01 |  | 321000 | 321000 |  |  | 30% | 69 | [8 empty] | 25.101 (c) (5) (A) | Distibution moved from work area. | 321000 | 0 | 321000 |  |  | 321000 | 0 | 0
704.2054, 804.2053 | Industrial Park Dbl. Ckt. | Wharton | Double circuit 69 kV tap | 2004-10-01 | 2005-02-01 |  | 275000 | 275000 |  |  | 30% | 69 |  | 0.33 | 795 ACSR | Single Pole | 50 | 0.33 | 0 | 0 | 25.101 (c) (5) (A) | One deadend peer set. Poles to be delivered in March | 275000 | 0 | 275000 |  |  | 275000 | 0 | 0
704.2102, 804.2101 | Corpus Christi Tap to Driscoll Sub | Nueces | Reconductor Static and replace insulators and hardware | 2004-08-01 | 2004-10-01 |  | 250000 | 250000 |  |  | 100% | 69 |  | 12.43 |  | Single Pole | 50 | 12.43 | 0 | 0 | 25.101 (c) (5) (B)(i) | Completed. Waiting on accounting. | 250000 | 0 | 250000 |  |  | 250000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
|  | NEW PROJECTS: | [20 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 4987000 | 4987000
[24 empty] | 0 | 18 | 18 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## SULP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
PR.03.05003.CAP | SULP 138 kV Transmission Lower Loop | Hidalgo County | New 138 kV Transmission line from Bentsen Tap, south to the new Bentsen Substation, west to proposed Railroad Substation and then north to Bryan Road Tap. | 2002-09-01 | 2005-03-31 |  | 3978000 |  |  |  | 94 | na | 138 kV | 4.63 | 1590 acss single conductor | Concrete and steel poles with Davit Arms | na | na | 80 | 4.63 | 24874 | Conductor terminations at Bentsen Substation done, needs to do jumpers on towers. Remaining portion of lower loop line complete except tie in with 138kv line sections to S. McAllen & Frontera Power Plant. | 3978000 | 0 | 3978000 |  |  | 3978000 | 0 | 0
PR.03.05051.CAP | Sharyland DC Interconnect with CFE | Hidalgo County | Install 150 MVA back to back HVDC interconnection with CFE at SU's Railroad Substation. | 2005-04-01 | 2006-12-31 |  | 0 |  |  |  | 0 | na | 138 kV | 0.8 | 795 acss single conductor | Concrete or Steel Poles |  |  | 80 | 0.8 | 28834 | Waiting on CCN approval. Projected. | 0 | 0 | 0 |  |  | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 3978000 | 3978000
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## SWEPCO
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
40022879 | Pittsburg to Winnsboro 138kV Line | Camp, Wood, Franklin | Construct approximately 20 miles of new 138kV transmission line using single pole with davit arm construction. | 2005-09-05 | 2006-03-03 | na | 7426000 |  |  |  |  | na | 138 | 20 | 1590 ACSR with Static | single pole steel or concrete with davit arms | na | na | 100 | 20 | 28104 | Received PFD | 7426000 | 0 | 7426000 |  |  | 7426000 | 0 | 0
40030820 | Winnsboro to N. Mineola | Wood | Construct approximately 25 miles of new 138kV transmission line using single pole with davit arm construction. | 2006-07-05 | 2007-11-01 | na | 9963000 |  |  |  |  | na | 138 | 25 | 1590 ACSR with Static | single pole steel or concrete with davit arms | na | na | 100 | 25 | 30128 | The CCN was filed on January 12, 2005. | 9963000 | 0 | 9963000 |  |  | 9963000 | 0 | 0
40398973 | International Paper Company (IPC) Reroute | Cass | Relocate 10 structures of the 69kV line for International Paper Company (IPC) | 2004-11-01 | 2004-12-15 | 2004-12-15 | 250000 |  |  |  | 100% | 69kV |  | 0.4 | 4/0 ACSR | wood single pole | 100 | 0.4 | 100 | 0.52 | 25.101(c)(5)(D) | IPC Paying tor relocation and provides easement | 250000 | 0 | 250000 |  |  | 250000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 17639000 | 17639000
[24 empty] | 0 | 3 | 3 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## TNMP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) | REQUESTED ADDITIONAL INFORMATION | Last Month: | Current minus last month: | Cumulative Sum
GCEC22521, GCEC22411 | Bp Amoco Interconection | Texas City, Texas | Contruction of new 138kV, 1-1/2 breaker switchyard and the upgrade of various other TNMP transmission lines and substations to provide for the interconnect of new Cogen to export 480MW onto the ERCOT grid. | 2002-10-01 |  |  | 15000000 |  |  |  | 82% | na | 138kV | 0.6 | 795 ACSS | Concrete | na | na | 50 | 1.7 | Rule 25.101(c)(2)(C)(i). Docket # 25970 | New Greenbelt switching station was energized on May 6 2003. Work continues on line upgrades. | 15000000 | 0 | 15000000 |  |  | 15000000 | 0 | 0
GCEC24517 | Part of Bp Amoco Interconection | Texas City, Texas | Rebuild circuit 138-1A, GAF to PH Robinson | 2005-01-10 |  |  | 2800000 |  |  |  | 30% | 138kV | n/a | 4 | 636ACSS | Concrete | 40 | 6 | n/a | n/a | Rule 25.83(c)(3) | Clearance taken on 1/10/05 | 2800000 | 0 | 2800000 |  |  | 2800000 | 0 | 0
GCEC24514 Staff A | Texas City Main 69KV Switchstation Rebuild and Transmission Lines | Texas City, Texas, Galveston County | Reroute and build one end of transmission line G69-E1from the old Texas City Main Switchstation to the new Texas City Main Switchstation | 2004-12-06 | 2004-12-14 | 2004-12-14 | 140000 | 140000 | 140000 | 0% | 100% | 69KV | na | 0.225 | 795 ACSR | Concrete | na | na | 80, street | 0.225 | Rule 25.83(c)(3), 25.101(C)(5) | Only rerouting one end of line into new replacement switchstation. STAFF: THIS PROJECT WAS REPORTED AS COMPLETE LAST MONTH AND SHOULD HAVE BEEN DELETED. | [5 empty] | 140000 | -140000 | -140000
GCEC24514 Staff B | Texas City Main 69KV Switchstation Rebuild and Transmission Lines | Texas City, Texas, Galveston County | Reroute and build one end of transmission line G69-F from the old Texas City Main Switchstation to the new Texas City Main Switchstation | 2004-12-21 | 2004-12-30 | 2005-01-24 | 61000 | 61000 | 61000 | 0% | 100% | 69KV | na | 0.08 | 795 ACSR | Concrete | na | na | 70, street | 0.08 | Rule 25.83(c)(3), 25.101(C)(5) | Only rerouting one end of line into new replacement switchstation. STAFF: THIS PROJECT WAS REPORTED AS COMPLETE LAST MONTH AND SHOULD HAVE BEEN DELETED. | [5 empty] | 61000 | -61000 | -201000
GCEC24514 Staff C | Texas City Main 69KV Switchstation Rebuild and Transmission Lines | Texas City, Texas, Galveston County | Reroute and build one end of transmission line G69-D2 from the old Texas City Main Switchstation to the new Texas City Main Switchstation | 2005-01-03 | 2005-02-04 | 2005-02-04 | 100000 | 100000 | 100000 | 0% | 100% | 69KV | na | 0.126 | 795 ACSR | Concrete | na | na | 100, street | 0.126 | Rule 25.83(c)(3), 25.101(C)(5) | Only rerouting one end of line into new replacement switchstation. | 100000 | 100000 | 0 |  |  | 100000 | 0 | -201000
GCEC25510 | New TNMP Amoco Substation to Cherokee Switching Station Transmission Line | Texas City, Texas, Galveston County | Engineer and construct new 138KV transmission line form the existing Amoco Substation to the new Cherokee Switchyard. | 2005-01-01 |  |  | 1500000 |  |  |  | 5% | 138KV | 138kV | 0.4 | 795 ACSS | Concrete | 60 | 0.4 | na | na | Rule 25.83(c)(3), 25.101(C)(5) | Line will be constructed in existing ROW and will share structures with tnmp circuit 69-C. | 1500000 | 0 | 1500000 |  |  | 1500000 | 0 | -201000
GCEC25520 | New TNMP Comanche Switching Station to Cherokee Switching Station Transmission Line | Texas City, Texas, Galveston County | Engineer and construct new 138KV transmission line form the existing Comanche to the new Cherokee Switchyard. | 2005-01-01 |  |  | 1500000 |  |  |  | 5% | 138KV | 138kV | 0.6 | 795 ACSS | Concrete | 60 | 0.4 | 60 | 0.2 | Rule 25.83(c)(3), 25.101(C)(5) | Line will use existing ROW and share structures with 69-C for about .4 miles. A new ROW of about .2 miles will be added along 14th Street. | 1500000 | 0 | 1500000 |  |  | 1500000 | 0 | -201000
WHIC22511 | Bosque Switch 138 kV Interconnect | Bosque County, Texas | Cut into TNMP's existing 138 kV line from Lake Whitney to Olsen Substations and build lines into & out of BEPC's Bosque Switch Station which serves Mirant's Bosque Power Plant | 2005-04-07 |  |  | 800000 |  |  |  | 0% | 138kV | 138kV | 0.54 | 795 ACSR | Concrete | 0 | 0 | 85 | 0.27 | Rule 25.83(c)(3), 25.101(C)(5) | Easement procurement has delayed the project. A new ROW is verbally agreed to by Mirant and negotiations are continuing. Mirant owns the land that TNMP requires a ROW across. | 800000 | 0 | 800000 |  |  | 800000 | 0 | -201000
[23 empty] | 0 | 0 | 0
NOTE: PUC STAFF ADDED IDENTIFIERS TO MAKE EACH OF THE THREE GCEC24514 PROJECT NUMBERS UNIQUE.
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 301000 | 100000 | 21600000 | 21700000
[24 empty] | 1 | 5 | 6 | Project Count
[24 empty] | Completed | Active | Total
Note on A4: Allen Steven Boling: PUC STAFF ADDED IDENTIFIER TO PROJECT NUMBER TO MAKE EACH OF THE THREE 24514 PROJECTS UNIQUE. ERRORS IN THE CHECK PROCESS RESULT OTHERWISE.
Note on A5: Allen Steven Boling: PUC STAFF ADDED IDENTIFIER TO PROJECT NUMBER TO MAKE EACH OF THE THREE 24514 PROJECTS UNIQUE. ERRORS IN THE CHECK PROCESS RESULT OTHERWISE.
Note on A6: Allen Steven Boling: PUC STAFF ADDED IDENTIFIER TO PROJECT NUMBER TO MAKE EACH OF THE THREE 24514 PROJECTS UNIQUE. ERRORS IN THE CHECK PROCESS RESULT OTHERWISE.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on X4: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.
Note on X5: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.
Note on Y4: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.
Note on Y5: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.
Note on Z4: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.
Note on Z5: Allen Steven Boling: FORMULA DELETED: THIS PROJECT WAS CLOSED IN THE JANUARY 2005 REPORT.

## TXU
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Sort | Last Month: | Current minus last month: | Cumulative Sum
00T64047 WB | N. Herty-E. Lufkin 138 kV: Reconductor Project | City of Lufkin | Reconductor 138 kV circuit from North Herty Switch Station to East Lufkin Substation with 1590 kcmil ACSR. Replace steel poles with hybrid concrete/steel poles. H-Frame portion will be rebuilt with single pole concrete construction. Steel tower portion of the line will be analyzed for the addition of a second circuit | 2006-01-02 | 2006-05-15 |  | 2033323 |  |  |  | 0 | 138 | na | 9.5 | 1590 kcmil ACSR | Concrete Poles | 100 | 9.5 | na | na | 25.101(C)(5)(B) | Project in-service date has been deferred to Summer 2006. | 2033323 | 0 | 2033323 |  |  | 1 | 2033323 | 0 | 0
05T65109 JO | Calumet - West Dallas 138 kV: Connect Westmoreland North Substation | City of Dallas, Dallas County | Relocate one existing steel pole and connect new substation. | 2005-03-01 | 2005-04-15 |  | 74400 |  |  |  | 0 | 138 | na | 0.2 | 795 kcmil ACSR | Steel Poles | 80 | 0.2 | na | na | 25.101(c)(5)(A) |  | 74400 | 0 | 74400 |  |  | 2
02T65124 BJP/MM 04T65148 JA/MM | Paris-Clarksville 69 kV: Rebuild | Red River County | This transmission line is being rebuilt in two sections. The first section extended from Bagwell to Clarksville and was completed during 2003. The second section will extend from Lamar Blossom to Bagwell and will be complete by the end of 2004. The construction will consist of wood poles, 336.4 kcmil ACSR conductor with no static. | 2003-06-01 | 2004-12-16 | 2004-12-16 | 2532734 | 2532734 |  |  | 100 | 69 | na | 19.11 | 336.4 kcmil ACSR | Wood Poles | na | 19.11 | na | na | 25.101(c)(5)(B) | The scope of this project has changed to include the extension to an additional section of this transmission line. Initial Estimated Project Cost has been revised. Final costs accumulating. | 2532734 | 0 | 2532734 |  |  | 3 | 2532734 | 0 | 0
03T65099 04T65234 04T65243 TW/RC | E. Richardson-Rowlett 138 kV: Rebuild | Dallas County | Project in two phases. First phase of construction will consist of rebuilding the existing 138 kV section from E. Richardson to Struct. 5/1. section, which includes 4 miles of single circuit and 1.2 miles of double circuit. The 2nd phase of construction consists of rebuilding the existing 138 kV section from Struct. 5/1 to Rowlett which includes 8.7 miles of single circuit and begins 12/01/03. | 2003-10-24 | 2005-03-01 |  | 16147581 | 15575553 |  |  | 90 | 138 | na | 13.9 | 1033.5 kcmil ACSR Bundled | Steel Poles | 80 | 12.7 | na | na | 25.101(c)(5)(B) | This project will be completed in 2 phases. | 15575553 | 0 | 15575553 |  |  | 4 | 15575553 | 0 | 0
03T64045 EH/JB | Whitney-Walnut Springs 138 kV | City of Whitney, Bosque County | Rebuild 17.5 miles of existing 336.4 kcmil ACSR conductor on wood H-frames with 795 kcmil ACSR on single concrete poles. | 2005-01-16 | 2005-04-15 |  | 4266000 | 4266000 |  |  | 5 | 138 | na | 17.5 | 795 kcmil ACSR | Concrete Poles | 100 | 17.5 | na | na | 25.101(c)(5)(B) |  | 4266000 | 0 | 4266000 |  |  | 5 | 4266000 | 0 | 0
03T65142 AK | Payne-Bonham 69 kV: Replace switches and switch structure at the Ector Substation tap point. | Fannin County | Remove wood switch structure and switches and replace with one single concrete pole switch structure with three switches. | 2004-05-17 | 2004-08-15 | 2004-08-15 | 114546 | 148000 |  |  | 100 | 69 | na | na | 336.4 kcmil ACSR | Concrete Pole | 130 | na | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 148000 | 0 | 148000 |  |  | 6 | 148000 | 0 | 0
03T63037 DRC/JE | Big Spring-Cosden-Falcon Seaboard COGEN 138 kV: Rebuild | City of Big Spring, Howard County | Replace existing structures, shield wire and conductors to provide a summer long term emergency rating of 1365 amperes per planning department requirements. |  |  |  | 1414596 |  |  |  | 0 | 138 | na | 1.29 | 1590 kcmil ACSR | Concrete Poles and Steel Poles | 50-60 | 1.29 | na | na | 25.101(c)(5)(B) | Deferred indefinitely due to ongoing negotiations with the customer concerning ownership of certain facilities. | 1414596 | 0 | 1414596 |  |  | 7 | 1414596 | 0 | 0
03T64049 RC/BW | Minerva-Robertson 138 kV: Rebuild | Robertson County and Milam County | Project in two phases. First phase of construction will consist of rebulding the existing 138 kV section from Minerva Substation to Milano Substation, which is 6.7 miles of single circuit. The second phase of construction consists of rebuilding the existing 138 kV section from Milano Substation to Robertson Substation, which is 20.9 miles of single circuit. | 2004-01-19 | 2004-10-11 | 2004-10-11 | 4445000 | 4445000 |  |  | 100 | 138 | na | 27.6 | 795 kcmil ACSR | Steel Poles or Concrete Poles | 100 | 27.6 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 4445000 | 0 | 4445000 |  |  | 8 | 4445000 | 0 | 0
03T65124 EH/AJ | Paris-Commerce 69 kV: Convert to 138 kV Operation | City of Commerce, City of Cooper, and the City of Paris, Hunt County, Delta County and Lamar County | Convert the existing 34.1 mile Paris Switch to Commerce Sub 69 kV 1033.5 kcmil ACSR on concrete single poles or H-frame structures to a double circuit 138/69 kV with 1033.5 kcmil ACSR on single concrete poles. Rebuild the existing 2.5 mile Commerce Sub to Commerce Switch 138 kV 336.4 kcmil ACSR on steel towers and wood H-frame structures with 1033.5 kcmil ACSR on existing steel towers and single concrete poles. | 2004-01-12 | 2004-12-23 | 2004-12-23 | 9400000 | 9400000 |  |  | 100 | 69 | 69138 | 70.7 | 1033.5 kcmil ACSR | Concrete Poles, Steel Towers, Wood H-Frames | 100 | 36.6 | na | na | 25.101(c)(5)(B), 25.101(c)(5)(C) | Final costs accumulating. | 9400000 | 0 | 9400000 |  |  | 9 | 9400000 | 0 | 0
03T65178 MM | Anna Sw Sta - McKinney Sub 138 kV | City of McKinney, Collin County | Rebuild 7.50 miles of existing double circuit single 795 kcmil ACSR and single 1033.5 kcmil ACSS conductor on steel poles and steel towers with bundled 1233.6 kcmil ACSS/TW on steel poles. | 2004-03-15 | 2004-11-19 | 2004-11-19 | 7390000 | 7380323 |  |  | 100 | 138 | na | 15 | 1233.6 kcmil ACSS/TW Bundled | Steel Poles | 100 | 7.5 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 7380323 | 0 | 7380323 |  |  | 10 | 7380323 | 0 | 0
03T65177 MM/JB | Allen Sw Sta - McKinney Sub 138 kV | City of McKinney, Collin County | Rebuild 13.50 miles of existing double circuit single 795 kcmil ACSR and single 1033.5 kcmil ACSS conductor on steel poles and steel towers with bundled 1233.6 kcmil ACSS/TW on steel poles. | 2004-09-15 | 2005-03-15 |  | 13400000 | 13400000 |  |  | 8 | 138 | na | 27 | 1233.6 kcmil ACSS/TW Bundled | Steel Poles | 100 | 13.5 | na | na | 25.101(c)(5)(B) |  | 13400000 | 0 | 13400000 |  |  | 11 | 13400000 | 0 | 0
03T61005 BW | Renner - W. Plano 138 kV: Relocation for Billingsley | City of Plano, Collin County | Relocate a portion (4200 ft.) of the Renner-W. Plano 138 kv Line to accommodate land development by the Crow-Billingsley Investment Company. This relocation consists of removing 8 double circuit steel lattice towers and installing 8 double circuit single steel poles (3400 ft.). This relocation is at the request of Crow-Billingsley Investment Company and is 100% reimburseable. | 2004-02-15 | 2004-09-02 | 2004-09-02 | 637148 | 637148 |  |  | 100 | 138 | na | 1.28 | 1033.5 kcmil ACSR | Steel Poles | 100 | 0.8 | 70 | 0.64 | 25.101(c)(5)(D) | This project is reimbursable by Crow-Billingsley. Final costs accumulating. | 637148 | 0 | 637148 |  |  | 12 | 637148.36 | -0.36 | -0.36
04T63022 JS/DRC | Midessa to Midland West 138 kV: Rebuild | City of Midland, Midland County | Replace existing structures, shield wire and conductors to provide a summer long term emergency rating of 1365 amperes | 2004-08-30 | 2004-10-22 | 2004-10-22 | 1675946 | 1546557 |  |  | 100 | 138 | na | 3.81 | 1590 kcmil ACSR | Steel Poles or Concrete Poles | 50-75 | 3.81 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 1546557 | 0 | 1546557 |  |  | 13 | 1546557 | 0 | -0.36
04T62072 04T62071 BM/BW | Benbrook-Wedgewood 138 kV No. 1 (South): Reconductor with 1233.6 ACSS/TW (04T62072) / Benbrook-Wedgewood 138 kV No.2 (North): Reconductor with 1233.6 ACSS/TW (04T62071) | Tarrant County | The project will consist of reconductoring the South (No.1) & North (No. 2) Circuit of the Benbrook-Forest Hill 138 kV DC line. The existing 795 kcmil ACSR conductor will be removed and new 1233.6 ACSS/TW will be installed. Other work to include the addition of one switch structure and a set of LDS line switches under each circuit. All work to be done within the existing TXU Electric Delivery ROW. No additional ROW will be required for this project. | 2004-03-18 | 2004-09-23 | 2004-09-23 | 2149670 | 2149670 |  |  | 100 | 138 | na | 5.65 | 1233.6 kcmil ACSS/TW | Steel Towers | 75 | 5.65 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 2149670 | 0 | 2149670 |  |  | 14 | 2149670 | 0 | -0.36
03T42014 BM/BW | Hillsboro - Waco Tap Line to Waco General Tire Substaion 69 kV: Relocate Sectionalizing from Waco-General Tire | City of Waco, McLennan County | This project is being constructed to establish a loop point at the Waco Katy Substation Tap. This project will consist of adding 3 switches on 2 Steel Mono-Poles. The new steel poles will be installed on the existing 69 kV centerline. No new ROW will be required. | 2004-06-01 | 2004-08-01 | 2004-08-01 | 129621 | 250000 |  |  | 100 | 69 | na | 0.01 | 336.4 kcmil ACSR | Wood Poles and Steel Poles | 70 | 0.01 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 250000 | 0 | 250000 |  |  | 15 | 250000 | 0 | -0.36
02T61013 BW/BM | Pflugerville South 138 kV: Reroute for Raw Water Storage | City of Pflugerville, Travis County | The City of Pflugerville has requested that a section of the Pflugerville South 138 kV line be relocated to accommodate their new Raw Water Storage facility. This relocation will involve removing 6 structures and the addition of 8 structures. The City of Pflugerville has granted TXU Electric Delivery an easment for the relocated Transmission line. | 2004-04-19 | 2004-08-15 | 2004-08-15 | 840000 | 1068961 |  |  | 100 | 138 | na | 0.54 | 1590 kcmil ACSR | Steel Poles | 50 | 0.54 | 50 | 0.54 | 25.101(c)(5)(F) | This project is reimbursable. Final costs accumulating. | 1068961 | 0 | 1068961 |  |  | 16 | 1068961 | 0 | -0.36
03T61015 BW/BM | Brownwood-Goldthwaite 138 kV: Relocate Along FM 3064 for TxDOT | Brown County | TxDOT has requested that a section of the Brownwood 138 kV Line be relocated for the widening of FM 3064 (Morris Shepard Drive). This Relocation will consist of relocating the existing 138 kV line approximatley 18' to the south. Five existing wood structures and two guyed steel poles will be removed and Four new tangent concrete and Two self supporting steel poles will be installed. The relocated transmission line will be relocated within Texas Department of Transportation ROW. | 2004-09-30 | 2004-10-20 | 2004-10-20 | 375000 | 415000 |  |  | 100 | 138 | na | 0.42 | 636. kcmil ACSR | Concrete Poles and Steel Poles | 50 | 0.42 | 50 | 0.42 | 25.101(c)(5)(F) | TxDOT has given TXU Electric Delivery consent to relocate the transmission line within TxDot ROW. All new ROW obtained is TxDOT ROW. This project is not reimbursable. Final costs accumulating. | 415000 | 0 | 415000 |  |  | 17 | 415000 | 0 | -0.36
04T62030 MM | Ft. Worth-Cleburne 69 kV: Replace Structure 501 in the Forest Hill-Burleson section | City of Ft. Worth, Tarrant County | Existing Structure 501 in the Ft. Worth-Cleburne 69 kV Line is a double circuit steel tower supporting one circuit of 336.4 ACSR conductor and one 3/8'' shield wire. During a recent inspection, it was discovered that one leg of the tower had been broken off by a tractor or some other piece of equipment. This structure will be replaced with a concrete pole. | 2004-09-23 | 2004-09-23 | 2004-09-23 | 44680 | 44680 | 18215 | -59% | 100 | 69 | na | na | 336.4 kcmil ACSR | Concrete Pole | 50 | na | na | na | 25.101(c)(5)(B) | Interim Report filed 03/04/2004. | 44680 | 44680 | 0 |  |  | 18 | 44680 | 0 | -0.36
03T62061A JB/EH | Seldon - Walnut Springs 138 kV | City of Walnut Springs, Bosque County | This project consists of rebuilding two separate line sections. First, rebuild Johnsville-Walnut Springs section, 12.20 miles of existing 4/0 ACSR conductor on wood H-frames with 795 kcmil ACSR on single concrete poles and concrete H-frames. Second, rebuild Seldon-Johnsville section, 13.2 miles of existing 4/0 ACSR conductor on wood H-frames with 795 kcmil ACSR on single concrete poles & concrete H-frames. | 2004-06-24 | 2004-12-29 | 2004-12-29 | 6456872 | 6456872 |  |  | 100 | 138 | na | 25.4 | 795 kcmil ACSR | Concrete Poles and Concrete H-Frames | 100 | 25.4 | na | na | 25.101(c)(5)(B) | This project was initially planned to be reported on 2 separate rows on this report, each row representing one rebuilt line section. To appropriately track project costs, it will be reported on one row. Data columns have been updated as necessary. Final costs accumulating. | 6456872 | 0 | 6456872 |  |  | 19 | 6456872 | 0 | -0.36
SEI/BW | Coppell-Apollo Rd 69 kV: Midway Rd and Keller Springs | City of Addison, Dallas County | Relocate and replace single wood angle pole for intersection improvements. | 2005-04-15 | 2005-04-30 |  | 15000 |  |  |  | 0 | 69 | na | 0.14 | 336.4 kcmil ACSR | Wood Pole | 0 | 0.14 | na | na | 25.101(c)(5)(F) | This is a Dallas County CMAQ project. The project is not reimbursable. | 15000 | 0 | 15000 |  |  | 20 | 15000 | 0 | -0.36
04T61001 SEI/BW | Hillsboro-Leon 138kV: Relocate for FM 2214 | City of Eastland, Eastland County | Relocate and replace 5 wood H-Frames with 5 concrete H-Frames. | 2004-12-06 | 2004-12-15 | 2004-12-15 | 139159 | 139159 |  |  | 100 | 138 | na | 0.54 | 336.4 kcmil ACSR | Wood H-Frames and Concrete H-Frames | 100 | 0.54 | na | na | 25.101(c)(5)(F) | Relocation at request of TxDOT to accommodate widening and reconstruction of FM 2214. This project is 100% reimbursable. Final costs accumulating. | 139159 | 0 | 139159 |  |  | 21 | 139159 | 0 | -0.36
04T61010 WB/LH | Liggett-Euless 138 kV: Upgrade Existing DFW South UG Line Section | DFW International Airport, Dallas County and Tarrant County | Install a second parallel HPFF 8" pipe and 3500 kcmil cable for both circuits between D-West and E-East, Approximately 2.67 miles. This project will establish two bundled 3500 kcmil UG circuits segments between the OH/UG Transition Stations Referenced. | 2004-09-16 | 2005-05-15 |  | 13350000 | 13350000 |  |  | 40 | 138 | na | 2.69 | 2-3500 kcmil copper, 138 kV paper insulated HPFF pipe type cable | Underground High Pressure Fluid Filled Pipe Type Sysyem | 30 | 2.69 | 25 | 2.69 | 25.101(c)(5)(B) |  | 13350000 | 0 | 13350000 |  |  | 22 | 13350000 | 0 | -0.36
04T65093WB/MH 04T65104WB/JO | Hackberry-Grapevine Ball St 138 kV Line: Rebuild Overhead Line Portion and Upgrade UG Line Portion Across DFW international Airport | Dallas County, Tarrant County, and Northern Area Of Dallas/Fort Worth International Airport | Rebuild 10.98 miles Hackberry-Grapevine Ball St.Overhead/Underground 138 kV Line. Rebuild 9.2 mile Overhead Portion With 1233.6 kcmil ACSS/TW and 1929.6 kcmil ACSS/TW Condcutor and Upgrade 1.78 mile Underground Pipe Type Cable System to a Parallel 3500 kcmil Pipe Type Cable System. | 2004-07-01 | 2005-05-15 |  | 7,773,360 (overhead) 11,241,270 (underground) | 19014630 |  |  | 35 | 138 | na | 10.98 | 1233.6 kcmil ACSS/TW, 1929.6 kcmil ACSS/TW, 2-3500 kcmil Copper, 138 kV Paper Insulated HPFF Pipe Type Cable | Steel H-Frames, Steel Poles, Lattice Steel Towers & Underground High Pressure Fluid Filled Pipe Type System | 100 & 50 on Overhead and 30 feet on Underground | 10.98 | 25 for underground portion only | 1.78 | 25.101c(5)(B) | Overhead portion of project on separate project number added to this line to show complete project. | 19014630 | 0 | 19014630 |  |  | 23 | 19014630 | 0 | -0.36
04T62043 AK | Grapevine Junction - Coppell 138 kV: Connect the Flower Mound South Substation | City of Flower Mound, Denton County | Replace 1-80' steel tangent pole with 2-95' steel self supporting 90 degree angle poles to connect the Flower Mound South Substation to the McKamy Tap portion of the Grapevine Juntion to Coppell 138 kV Transmission Line. | 2004-07-01 | 2004-08-05 | 2004-08-05 | 414513 | 326611 |  |  | 100 | 138 | na | na | 795 kcmil ACSR | Steel Poles | 50 | na | na | na | 25.101(c)(5)(A) | Final costs accumulating. | 326611 | 0 | 326611 |  |  | 24 | 326611 | 0 | -0.36
03T65130 MM | Greenville Ave.-800/900 Network 138 kV | City of Dallas, Dallas County | Reconductor the 138 kV double circuit from Greenville Ave. Substation to just outside the existing Flynn Street 138 kV Overhead to Underground Terminal Station with 1233.6 kcmil ACSS/TW conductor. The existing lattice steel structures will be modified, upgraded or replaced as necessary to support the larger conductor. In 2005, the Flynn Street Terminal Station will be decommissioned and a new terminal will be established at 800/900 Network Substation. At present, there is an overhead double circuit 138 kV tie between 800/900 Network Substation and the Flynn Street Terminal. When the Flynn Street Terminal is decommissioned, the circuits will be rearranged such that they will bypass the Flynn Street Terminal and continue on to the 800/900 Network Substation on the existing structures. | 2004-10-15 | 2004-12-22 | 2004-12-22 | 3344949 | 3344949 |  |  | 100 | 138 | na | 4.92 | 1233.6 kcmil ACSS/TW | Steel Towers, Steel Poles and Concrete Poles | 60 - 100 | 4.92 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 3344949 | 0 | 3344949 |  |  | 25 | 3344949 | 0 | -0.36
04T63028 JS/DRC | Odessa EHV - TI Tap 138 kV: Rebuild | City of Odessa, Ector County | Replace existing structures, shield wire and conductors as required to provide a summer long term emergency rating of 1365 amperes | 2004-08-30 | 2004-12-30 | 2004-12-30 | 3078864 | 3449004 |  |  | 100 | 138 | na | 8.91 | 1590 kcmil ACSR | Concrete Poles and Steel Poles | 75 | 8.91 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 3449004 | 0 | 3449004 |  |  | 26 | 3449004 | 0 | -0.36
04T62086 04T62087 BM/WB | Calmont-Benbrook 138 kV (East): Reconductor with 1233.6 kcmil ACSS/TW (04T62086) / Calmont- Benbrook 138 kV (West): Reconductor with 1233.6 kcmil ACSS/TW (04T62087) | Tarrant County | The project will consist of reconductoring the East & West Circuit of the Calmont-Benbrook 138 kV DC line. The existing 1798 kcmil ACAR conductor will be removed and new 1233.6 kcmil ACSS/TW will be installed. Other work to include the raising of steel towers for high temperature operation. All work to be done within the existing TXU Electric Delivery ROW. | 2004-09-20 | 2004-11-02 | 2004-11-02 | 1624601 | 1624601 |  |  | 100 | 138 | na | 4.67 | 1233.6 kcmil ACSS/TW | Steel Towers | 75 | 4.67 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 1624601 | 0 | 1624601 |  |  | 27 | 1624601 | 0 | -0.36
04T62055 BM/WB | Forest Hill - Everman 138 kV: Reconductor with 959.6 kcmil ACSS/TW | Tarrant County | This project will consist of reconductoring the South Circuit of the Forest Hill - Everman 138 kV line. The existing 795 kcmil ACSR will be removed and new 959.6 kcmil ACSS/TW will be installed. All work to be done within the existing TXU Electric Delivery ROW. | 2004-08-07 | 2004-08-16 | 2004-08-16 | 332269 | 332269 |  |  | 100 | 138 | na | 1.88 | 959.6 kcmil ACSS/TW | Steel Towers | 150 | 1.88 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 332269 | 0 | 332269 |  |  | 28 | 332269 | 0 | -0.36
04T65153 BM/WB | Watermill-Tricorner 345 kV: Reconductor with bundled 959.6 kcmil ACSS/TW | Dallas County | This project will consist of reconductoring the North Circuit of the Watermill-Tricorner 345 kV line. The existing bundled 795 kcmil ACSR will be removed and new bundled 959.6 kcmil ACSS/TW will be installed. Other work to include raising steel towers for high temperature operation. All work to be done within the existing TXU Electric Delivery ROW. | 2004-09-01 | 2004-11-16 | 2004-11-16 | 3592039 | 2750000 |  |  | 100 | 345 | na | 11.44 | 959.6 kcmil ACSS/TW Bundled | Steel Towers | 175 | 11.44 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 2750000 | 0 | 2750000 |  |  | 29 | 2750000 | 0 | -0.36
04T62056 JB/EH | Roanoke to Keller 138 kV: Rebuild | City of Keller, Tarrant County | Rebuild both circuits of the double circuit Roanoke-Keller (BEC) portion of the Roanoke-Euless 138 kV line. The length of the line to be rebuilt is approximately 3.71 miles. The existing single 1033.5 kcmil ACSR conductor will be replaced with bundled 1033.5 kcmil ACSR conductor. | 2004-09-15 | 2005-02-28 |  | 3810000 | 3810000 |  |  | 90 | 138 | na | 7.41 | 1033.5 kcmil ACSR Bundled | Steel Poles | 100 | 3.71 | na | na | 25.101(c)(5)(B) |  | 3810000 | 0 | 3810000 |  |  | 30
03T65100 04T65235 RC/TW | Rowlett - Rockwall 138 kV: Rebuild | City of Rowlett, City of Dallas and City of Rockwall, Dallas County and Rockwall County | This work covers the rebuild of the existing 138 kV double circuit line from Rowlett to Rockwall, which is 5.8 miles in length | 2004-08-09 | 2005-01-16 | 2005-01-16 | 9017494 | 9017494 |  |  | 100 | 138 | na | 11.6 | 1033.5 kcmil ACSR Bundled (On Circuit to be Upgraded) and existing 795 kcmil ACSR (on Circuit not Upgraded) | Steel Poles | 80 | 5.8 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 9017494 | 0 | 9017494 |  |  | 31 | 9017494 | 0 | -0.36
03T64048 RC/BW | Sandow-Minerva 138 kV: Rebuild | Milam County | Rebuild existing single circuit wood pole line. Replace single wood poles with single steel poles to accomodate a larger conductor. | 2004-09-02 | 2005-03-01 |  | 4445000 | 5714000 |  |  | 85 | 138 | na | 17.3 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 17.3 | na | na | 25.101(c)(5)(B) |  | 5714000 | 0 | 5714000 |  |  | 32 | 5714000 | 0 | -0.36
04T65119 04T65236 VZ/TW | Liggett-Collin 138 kV:Rebuild for increased capacity | City of Frisco and the City of The Colony, Collin County and Denton County. | Replace wood H-frames with single steel poles and single 1590 kcmil conductor from Collin SES to The Colony section of the Liggett-Collin 138 kV line. | 2004-09-21 | 2005-01-09 | 2005-01-09 | 8300000 | 8300000 |  |  | 100 | 138 | na | 9.47 | 1590 kcmil ACSR | Steel Poles | 100 | 9.47 | na | na | 25.101(c)(5)(B) | Interim Report filed 6/23/04. Final costs accumulating. | 8300000 | 0 | 8300000 |  |  | 33 | 8300000 | 0 | -0.36
04T62104 JLA | Comanche Peak - DeCordova 138 kV Line: Replace Structures 6/5 and 6/6. | City of Glen Rose, Somervell County | Replace two existing H-frame structures. Existing wood poles are split, replace with concrete poles. | 2004-10-15 | 2004-11-01 | 2004-11-01 | 95768 | 95768 |  |  | 100 | 138 | na | 0.1 | 795 kcmil ACSR | Concrete H-Frames | 100 | 0.1 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 95768 | 0 | 95768 |  |  | 34 | 95768 | 0 | -0.36
04T65170 SEI/BW | Coppell-Apollo Rd 69kV:Relocate for Sandy Lake Road | City of Coppell,Dallas County | Relocate and replace two wood poles for widening of Sandy Lake Road. | 2004-12-16 | 2004-12-22 | 2004-12-22 | 25058 | 25058 |  |  | 100 | 69 | na | 0.24 | 4/0 ACSR | Wood Pole | 50 | 0.24 | na | na | 25.101(c)(5)(F) | Project requested by City of Coppell. Project is not reimbursable. Final costs accumulating. | 25058 | 0 | 25058 |  |  | 35 | 25058 | 0 | -0.36
04T61019 SEI/BW | Decatur-Chico 69kV: Relocate for US 380 | City of Decatur, Wise County | Remove four single wood poles and replace with one concrete H-Frame and three single concrete poles to accommodate increased TxDOT ROW. The three single conrete poles with be relocated on new ROW. | 2005-04-01 | 2005-04-30 |  | 49684 | 258718 |  |  | 0 | 69 | na | 0.15 | 1/0 ACSR | Wood Pole | 100 | 0.15 | 100 | 0.15 | 25.101(c)(5)(F) | Project requested by TxDOT and is reimbursable. Project description and other data fields on January 2004 report have been revised due to change in project scope. | 258718 | 0 | 258718 |  |  | 36 | 258718 | 0 | -0.36
04T64044 AK | Corsicana Tap 138 kV: Connect BEPC Chatfield Substation | Navarro County | Replace two wood-H-frames with two concrete-H-frames and connect to the new BEPC Chatfield Substation dead end | 2004-10-15 | 2004-10-30 | 2004-10-30 | 66273 | 66273 |  |  | 100 | 138 | na | 0.15 | 336.4 kcmil ACSR Bundled | Concrete H-Frames | 100 | 0.15 | na | na | 25.101(c)(5)(A) | Work being done at request of Brazos Electric Power Cooperative, Inc. Final costs accumulating. | 66273 | 0 | 66273 |  |  | 37 | 66273 | 0 | -0.36
04T65116 AK | Forney-Royse 138 kV: Connect FEC Forney West Substation | City of Forney, Kaufman County | Replace two wood-H-frames with two concrete-H-frames and provide switches and switch structure for the FEC tap to the FEC Forney West Substation | 2004-12-12 | 2004-12-17 | 2004-12-17 | 188398 | 188398 |  |  | 100 | 138 | na | 0.2 | 795 kcmil ACSR | Concrete H-Frames | 100 | 0.2 | na | na | 25.101(c)(5)(A) | Work being done at request of Farmers Electric Cooperative. Final costs accumulating. | 188398 | 0 | 188398 |  |  | 38 | 188398 | 0 | -0.36
04T64045 JK/BW | Killeen Sw. Sta.-Killeen Taft St.138 kV: Add second circuit | Bell County | Add 2nd circuit of 795 kcmil ACSR on steel towers and steel poles | 2004-11-22 | 2004-12-31 | 2004-12-31 | 395000 | 690000 |  |  | 100 | 138 | na | 5.2 | 795 kcmil ACSR | Steel Pole | 100 | 5.2 | na | na | 25.101(c)(5)(C) | Final costs accumulating. | 690000 | 0 | 690000 |  |  | 39 | 690000 | 0 | -0.36
04T64092 WB/RG | West Waco-Belton 138 kV:Rebuild the Belton to North Temple line section | City of Belton and City of Temple, Bell County | Rebuild the 8.85 mile Belton - North Temple 138kV line section with single 1590 kcmil ACSR conductor. The 8.85 miles is made up of 7.25 miles on double circuit steel structures with two circuits in place and 1.6 miles on triple circuit steel H-frame structures with two TXU circuits in place and a third circuit (795 ACSR) from Brazos transferred to the new structures. | 2005-01-16 | 2005-06-01 |  | 5454226 | 5753601 |  |  | 5 | 138 | na | 17.7 | 1590 kcmil ACSR | Steel Poles and Steel H-Frames | 100 | 8.85 | na | na | 25.101(c)(5)(B) 25.101(c)(5)(C) |  | 5753601 | 0 | 5753601 |  |  | 40 | 5454226 | 299375 | 299374.64
04T61002 BJP/WB | Benbrook-Forest Hill 138 kv Line: Alcon Indus. Radial Taps | City of Fort Worth, Tarrant County | Construct a double ckt. self-supporting single steel pole line into a new customer-owned substation. | 2004-09-21 | 2004-12-22 | 2004-12-22 | 994015 | 1094100 |  |  | 100 | 138 | na | 0.6 | 336.4 kcmil ACSR | Steel Poles | na | na | 55 | 0.6 | 25.101(c)(5)(A) | Final costs accumulating. | 1094100 | 0 | 1094100 |  |  | 41 | 1094100 | 0 | 299374.64
04T42035 BM/BW | Milford Exxon Tap: Add 69 kV Line switched | City of Milford, Ellis County | Construction will consist of installing a self supporting steel pole switch tap structure and one additional concrete pole in an existing 69 kV double circuit steel tower transmission line between the Hillsboro Substation and the Waxahachie Substation and one additional tangent concrete pole in the Milford Exxon tap line. The construction will include removing one double circuit steel tower, one wood H-frame tap structure, one wood shield wire pole with guy wires, and a wood H-frame switch structure with guy wires. The line will be designed for 336 kcmil ACSR but the existing #1-3 strand copper wire will be reused. The line will be re-energized at 69 kV. The rebuild will be within the existing ROW. | 2004-11-16 | 2005-01-17 | 2005-01-17 | 163406 | 163406 |  |  | 100 | 69 | na | 0.35 | #1-3 strand copper | Concrete Poles and Steel Poles | 50 | 0.35 | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 163406 | 0 | 163406 |  |  | 42 | 163406 | 0 | 299374.64
04T64037 AK | Lake Creek-Whitney 138 kV: Reroute into the BEPC Bosque Switching Station | Bosque County | Remove five wood-H-frames and .43 miles of single circuit 336.6 kcmil ACSR conductor into the BEPC Whitney Switching Station and reroute into the BEPC Bosques Switching Station by adding one concrete-H-frame, one 90degree angle tower, six single concrete poles and .07 miles of single circuit 336.6 kcmil ACSR conductor. | 2005-04-15 | 2005-04-30 |  | 276598 | 276598 |  |  | 0 | 138 | na | 0.07 | 336 kcmil ACSR | Concrete Poles and Concrete-H-Frames | 100 | 0.07 | 75 | 0.06 | 25.101(c)(5)(A) | .06 miles of easement acquired from Brazos Electric Power Cooperative and .01 miles of new construction on existing easement. .43 miles of existing easement will be released after the completion of the project. Preliminary work will begin in 2004 but the main construction will not begin until 2005. | 276598 | 0 | 276598 |  |  | 43 | 276598 | 0 | 299374.64
04T65201 AK | Anna Switch-Anna Tap 138 kV: Provide Point of Interconnection to the Grayson County Electric Cooperative's Melissa Substation | Collin County | Install one self supporting steel pole switch structure with three switches to provide a Point of Interconnection and sectionalizing for the proposed Grayson County Electric Cooperative's Melissa Substation. | 2005-06-01 | 2005-06-15 |  | 192601 |  |  |  | 0 | 138 | na | na | 795 kcmil ACSR | Steel Pole | 150 | na | na | na | 25.101(c)(5)(A) |  | 192601 | 0 | 192601 |  |  | 44 | 192601 | 0 | 299374.64
04T62139 AK | Eagle Mountain-Wichita Falls 138 kV: Connect BEPC Carter Substation | Montague County | Replace two wood-H-frames with two concrete-H-frames and connect to the new BEPC Carter Substation dead end | 2005-03-15 | 2005-03-30 |  | 65143 |  |  |  | 0 | 138 | na | 0.15 | 636 kcmil ACSR | Concrete-H-Frames | 100 | 0.15 | na | na | 25.101(c)(5)(A) | Project at request of Brazos Electric Power Cooperative, Inc. | 65143 | 0 | 65143 |  |  | 45 | 65143 | 0 | 299374.64
04T62142 FC/EH 04T62143 FC/EH | Benbrook-Mistletoe 138 kV:Rebuild | City of Fort Worth and the City Benbrook, Tarrant County | Rebuild the double circuit Benbrook-Mistletoe 138kV Line. The existing structures are to be removed and replaced with double-circuit steel poles. | 2004-12-28 | 2005-05-01 |  | 12090664 | 12779717 |  |  | 10 | 138 | na | 19.6 | 1926.9 kcmil ACSS/TW | Steel Pole and Steel Towers | 75 | 9.8 | na | na | 25.101(c)(5)(B) | This project consists of Project Nos. 04T61020 and 04T61022 and therefore has been combined to one line item. | 12779717 | 0 | 12779717 |  |  | 46 | 12779717 | 0 | 299374.64
04T61025 BW/BM | Salado - Roundrock 138 kV Line:Relocate for SH-130 Near Gabriel Tap | Williamson County | TTA (Texas Turnpike Authority) is in the process of constructing the SH130 toll road, therefore TXU must replace 3 existing wood H-frame structures with 3 new taller steel pole H-frame structures. All structures to be raised and relocated will be on the existing TXU centerline. These structures must be raised to provide adequate vertical clearance over the proposed SH-130 bridge and Georgetown railroad. All cost associated with this project will be reimbursed to TXU. | 2004-12-01 | 2004-12-13 | 2004-12-13 | 342258 | 265250 |  |  | 100 | 138 | na | 0.28 | 795 kcmil ACSR | Wood H-Frames and Steel H-Frames | 100 | 0.28 | na | na | 25.101(c)(5)(F) | Final costs accumulating. | 265250 | 0 | 265250 |  |  | 47 | 265250 | 0 | 299374.64
04T61026 BW/BM | Pflugerville - Gilleland 138 kV line:Relocate for SH-130 at Pfluger Lane | Travis County | The Texas Turnpike Authority (TTA) is responsible for constructing the SH130 toll road that will connect I-35 at Georgetown to I-10 in Seguin. The construction of SH130 will necessitate that the Pflugerville - Gilleland 138 kV line be raised such that the TXU transmission facilities will have adequate vertical clearance above the proposed SH130 road and railway. All four structures to be raised and relocated will be done within the existing TXU Electric Delivery ROW. All cost associated with this project will be reimbursed to TXU Electric Delivery. | 2004-12-01 | 2004-12-17 | 2004-12-17 | 478549 | 495765 |  |  | 100 | 138 | na | 0.26 | 1590 kcmil ACSR | Steel poles | 45 | 0.26 | na | na | 25.101(c)(5)(F) | Final costs accumulating. | 495765 | 0 | 495765 |  |  | 48 | 495765 | 0 | 299374.64
04T62113 JLA | Decatur - Krum 69 kV Line: Provide 69 KV POI for BEPC's Allison Substation | Wise County | Remove structure 49/5 to accommodate substation deadend. | 2004-12-16 | 2004-12-23 | 2004-12-23 | 20000 | 46700 |  |  | 100 | 69 | na | 0.1 | 4/0 ACSR | Wood H-Frame | 50 | 0.1 | na | na | 25.101(c)(5)(A) | Interim report filed 10/29/2004. Final costs accumulating. | 46700 | 0 | 46700 |  |  | 49 | 46700 | 0 | 299374.64
04T61032 SEI/BW | Milford-Humble 69kV Tap Line: IH 35 at Mill Creek Bridge | City of Milford, Ellis County | Relocate and replace two wood H-Frame's with concrete H-Frame's for raising of Mill Creek bridge at IH 35. | 2005-01-16 | 2005-01-20 | 2005-01-20 | 69000 | 104638 |  |  | 100 | 69 | na | 0.34 | 4/0 ACSR | Concrete H-Frame | 100 | 0.34 | na | na | 25.101(c)(5)(F) | Interim Report filed 10/29/2004. Work being done at request of TxDOT. Project is reimbursable. Final costs accumulating. | 104638 | 0 | 104638 |  |  | 50 | 104638 | 0 | 299374.64
04T65122 AJ/MMW | Valley-Paris 138 kV:Rebuild from Paris Switch to Brookston | Lamar County | Rebuild the existing Paris Switching Station to Brookston Substation portion of the Valley to Paris138 kV Transmission Line. The existing conductor and wire will be rebuilt with 959.6 kcmil ACSS/TW on existing steel towers and single concrete poles. | 2005-01-17 | 2005-05-15 |  | 2100000 | 2058867 |  |  | 2 | 138 | 138 | 7 | 959.6 kcmil ACSS/TW | Concrete Poles | 100 | 7 | na | na | 25.101(c)(5)(B) |  | 2058867 | 0 | 2058867 |  |  | 51 | 2058867 | 0 | 299374.64
04T65120 RC/WB | Flynn Street 138kV UG & OH to establish East Levee-North Network | City of Dallas, Dallas County | Establish a new double circuit 138kV transmission line from East Levee to North Network with underground and overhead construction. | 2005-04-01 | 2005-09-15 |  | 3306315 |  |  |  | 0 | 138 | na | UG: 0.27 OH: 0.36 | UG: HPFF Pipe-Type 3500 kcmil Copper OH: 795 kcmil ACSS | Steel Pole | UG: 50 OH: 180 | UG: 0.27 OH: 0.36 | na | na | 25.101(c)(5)(A) |  | 3306315 | 0 | 3306315 |  |  | 52 | 3306315 | 0 | 299374.64
04T65224 JFO/WB | Liggett-Euless 138kV:Repairs to Faulted Underground Cable | City of Euless, Tarrent County | This project covers emergency repairs of TXU Electric Delivery south 138 kV Underground Transmission Line between DFW Southwest Airport and DFW D West Terminal Station. The failure occurred in the cable under Mid Cities Blvd., which required the installation of two manholes and the replacement of 125 feet of steel pipe and cable. | 2004-10-22 | 2004-11-15 | 2004-11-15 | 931637 | 931637 |  |  | 100 | 138 | na | 0.024 | HPFF Pipe-Type 3500 kcmil Copper | High Pressure Fluid Filled Cable System | 30 | 0.024 | na | na | 25.101(c)(3) | Emergency Repairs to Faulted Cable began as soon as posible to expidite restoration of the Liggett Euless 138 kV south circuit which provides one source to DFW Airport. Final costs accumulating. | 931637 | 0 | 931637 |  |  | 53 | 931637 | 0 | 299374.64
04T65182 MH/BW | Royse Switching Station - Lavon Substation 138kv: Rebuild Project | City of Royse City and the City of Lavon,Rockwall County and Collin County | Rebuild the 11 mile 138kV transmission line from the Royse Switching Station to the Lavon Substation. Using 1926.9 kcmil ACSS/TW conductor. | 2005-02-16 | 2005-12-15 |  | 5606751 | 5606751 |  |  | 0 | 138 | na | 11 | 1926.9 kcmil ACSS/TW | Steel Pole and Steel Towers. | 100 | 11 | na | na | 25.101(c)(5)(B) |  | 5606751 | 0 | 5606751 |  |  | 54 | 5606750.51 | 0.49 | 299375.13
04T61017 SEI/BW | Hillsboro-Leon 138kV:TXDOT relocation at FM 8 | City of Lingleville and Erath County | Relocate and replace two wood H-Frame's with concrete H-Frame's to accommodate increased TxDOT ROW. | 2005-01-21 | 2005-01-28 | 2005-01-28 | 67460 | 108156 |  |  | 100 | 138 | na | 0.35 | 4/0 ACSR | Wood H-Frame | 100 | 0.35 | na | na | 25.101(c)(5)(F) | Relocation requested by TxDOT. Project is reimbursable. Final costs accumulating. | 108156 | 0 | 108156 |  |  | 55 | 67460 | 40696 | 340071.13
04T61015 SEI/BW | Liggett-Saginaw 138kV:Transmission adjustments at SH 183 and SH 161 | City of Irving,Dallas County | Remove a 130' tangent steel/concrete hybrid pole and replace with a 130' steel DE pole; remove two 135' tangent steel/concrete hybrid poles and replace with two 195' tangent steel poles; remove a 105' steel/concrete tangent pole and replace with a 105' steel DE pole to achieve conductor clearance over new TxDOT interchange ramp. | 2005-02-16 | 2005-03-16 |  | 486479 | 486479 |  |  | 0 | 138 | na | 0.82 | 1033.5 kcmil ACSR Bundled | Steel and Concrete Hybrid Poles | 150 | 0.41 | na | na | 25.101(c)(5)(F) | Relocation requested by TxDOT. Project is reimbursable. | 486479 | 0 | 486479 |  |  | 56 | 486479 | 0 | 340071.13
04T61016 SEI/BW | Liggett-Hackberry 138kV:Transmission adjustments at SH 183 and SH 161 | City of Irving,Dallas County | Remove remove two 130' tangent steel/concrete hybrid poles and replace with two 195' tangent steel poles; remove a 105' steel/concrete tangent pole and replace with a 105' steel DE pole to achieve conductor clearance over new TxDOT interchange ramp. | 2005-02-16 | 2005-03-16 |  | 587055 | 587055 |  |  | 0 | 138 | na | 1 | 1033.5 kcmil ACSR Bundled | Steel and Concrete Hybrid Poles | 150 | 0.5 | na | na | 25.101(c)(5)(F) | Relocation requested by TxDOT. Project is reimbursable. | 587055 | 0 | 587055 |  |  | 57 | 587055 | 0 | 340071.13
04T65029 SEI/BW | E. Levee-Amelia St 138kV:Transmission adjustments at Reagan Street and Harry Hines Blvd | City of Dallas,Dallas County | Remove steel pole T-219 from median and replace with new steel pole on east side of Harry Hines outside of the Reagan Street Substation. | 2005-02-16 | 2005-03-01 |  | 70847 | 92373 |  |  | 0 | 138 | na | 0.1 | 795 kcmil ACSR | Steel Pole | 0 | 0.1 | na | na | 25.101(c)(5)(F) | Relocation requested by City of Dallas. Project is not reimbursable. | 92373 | 0 | 92373 |  |  | 58 | 70847 | 21526 | 361597.13
05T64020 WB/BM | Lake Creek: Install 2nd 345kV/138kV, 600 MVA Auto | McLennan County | Construction will consist of installing an overhead bus tie from Lake Creek Switching Station to Lake Creek Substation. This will include installing one dead end lattice steel transmission tower and approximately 800' of single circuit bundled 959.6 kcmil ACSS/TW. | 2005-02-15 | 05/014/2005 |  | 186826 | 186826 |  |  | 0 | 138 | na | 0.15 | 959.6 kcmil ACSS/TW Bundled | Steel Tower | na | na | 100 | 0.15 | 25.101(c)(5)(A) |  | 186826 | 0 | 186826 |  |  | 59
04T64098 BJP/MM | Ennis South-Ennis Southeast 138 kV Tap Line | City of Ennis,Ellis County | Construct a 138 kV tap line from the Ennis South-Ennis West 138 kV line to the new Ennis Southeast Substation utilizing double circuit self-supporting single concrete poles. A portion of the line will occupy the right of way of the existing Ferris-Corsicana 69 kV Transmission Line. The Ennis South-Ennis Southeast 138 kV Transmission Line will be constructed as double circuit configuration initially. In the section where it will occupy the right of way of the existing Ferris-Corsicana 69 kV Transmission Line, the existing structures supporting the 69 kV line will be removed and replaced with new steel and concrete poles. The 69 kV circuit will be transferred to the new poles and the 138 kV circuit will occupy the other side of the structures. When demand and reliability conditions dictate, a second 138 kV circuit will be added to the structures to create a loop to the proposed Ennis Southeast Substation. Consequestly, the line will be constructed such that it will ultimately support three circuits. | 2005-03-15 | 2005-04-15 |  | 2041000 |  |  |  | 0 | 69 | 138 | 5.06 | 795 kcmil ACSR | Concrete Poles and Steel Poles | 50,70 | 2.19 | 30 | 0.68 | 25.101(c)(5)(A) 25.101(c)(5)(B) |  | 2041000 | 0 | 2041000 |  |  | 60 | 2041000 | 0 | 361597.13
05T61001 JF/BW | Elkton - Tyler 138kV: Relocation for WalMart | City of Tyler, Smith County | Re-route approximately 3000 feet of existing wood H-frame transmission line to accommodate the construction of a new WalMart (Store No. 1044-01) | 2005-06-01 | 2005-08-01 |  | 947300 |  |  |  | 0 | 138 | na | na | 1590 kcmil ACSR | Steel Poles | 100 | na | na | na | 25.101(c)(5)(B) |  | 947300 | 0 | 947300 |  |  | 61 | 947300 | 0 | 361597.13
04T64141 AK | Stryker Creek-Nacogdoches 138kV: Replace structure 36/10 with a steel tower | City of Cushing,Nacogdoches County | Replace wood pole angle structure with a steel tower because wood poles and guys being effected by the increase in size of a nearby creek. | 2005-05-01 | 2005-05-15 |  | 5606751 |  |  |  | 0 | 138 | na | na | 636 kcmil ACSR | Steel Tower | 100 | na | na | na | 25.101(c)(5)(C) |  | 5606751 | 0 | 5606751 |  |  | 62 | 5606750.51 | 0.49 | 361597.62
04T61030 BM/BW | Taylor-Travis County 138 kV Line: Wood-H-Frame Relocation for SH 130 | Williamson County | TXDOT is in the process of constructing the new SH 130 toll way. Wood-H-frames along the Taylor - Travis County 138 kV line must be relocated within their existing centerline and raised to maintain vertical clearance over the new roadway. In order to raise the line for wood-H-frame structures must be removed and four new concrete-H-frame structures installed. The new construction will be placed in the existing centerline of the existing 138 kV line. No new ROW will be required for this relocation. | 2005-03-15 | 2005-05-15 |  | 101708 |  |  |  | 0 | 138 | na | 0.29 | 795 kcmil ACSR | Concrete H-Frames | 100 | 0.29 | na | na | 25.101(c)(5)(F) | All costs associated with this project will be reimbursed by Lone Star Infrastructure. | 101708 | 0 | 101708 |  |  | 63 | 101708 | 0 | 361597.62
05T61053 WB/BM | North Main SES - Denton Avenue 69 kV: Relocate Transmission Facilities for Tarrant County College | City of Fort Worth, Tarrant County | Tarrant County College has purchased a portion of the existing TXU property surrounding the North Main SES, North Main Substation and Heritage Substation. Accordingly, the North Main SES - Denton 69 kV line must removed out of the land purchased from TXU. The 69 kV Circuit will be continued into Heritage Substation. Approximately 2500' of new 795 kcmil ACSR will be installed. A vertical break switch with vacuum interrupters and buggy whip has been included in this WA. Two new tangent steel poles and one dead end angle pole have also been included in this estimate. | 2005-03-15 | 2005-05-15 |  | 366642 |  |  |  | 0 | 69 kV | na | 0.19 | 795 kcmil ACSR | Steel Poles | 50 | 0.32 | 50 | 0.19 | 25.101(c)(5)(E) | This project is reimbursable. | 366642 | 0 | 366642 |  |  | 64 | 366642 | 0 | 361597.62
05T61054 WB/BM | North Main - Saginaw 138 kV: Relocate Transmission Facilities for Tarrant County College | City of Fort Worth, Tarrant County | Tarrant County College has purchased a portion of the existing TXU property surrounding the North Main SES, North Main Substation and Heritage Substation. Accordingly, the North Main SES - Saginaw 138 kV line must be re-routed out of the land purchased from TXU. This work will include removing approximately 4000' of 795 kcmil ACSR and installing approximately 4000' of new 795 kcmil ACSR conductor. Other work will include installing a three pole angle structure, an "H" frame switch structure, two tangent steel poles and one set of 138 kV LDS switches. All project costs will be reimbursed. | 2005-03-15 | 2005-05-15 |  | 366671 |  |  |  | 0 | 138 kV | na | 0.19 | 795 kcmil ACSR | Steel Poles | 50 | 0.23 | 50 | 0.19 | 25.101(c)(5)(E) |  | 366671 | 0 | 366671 |  |  | 65 | 366671 | 0 | 361597.62
04T61018 BM/BW | Cedar Hill (DP&L)-Sterrett 138 kV Line: Relocate for TXI railroad spur | Ellis County | TXI has requested that a portion of the Cedar Hill (DP&L) - Sterrett 138 kV line from structure 21/1 to 21/10 be relocated to accommodate a new rail spur that TXI is installing. This project proposes to relocate the line as requested by TXI. The project will be reimbursed by TXI and all new ROW for this relocation will be supplied by TXI. | 2005-03-15 | 2005-05-15 |  | 208559 |  |  |  | 0 | 138 kV | na | 0.6 | 795 kcmil ACSR | Steel Poles and Concrete Poles | 100 | 0.6 | 100 | 0.6 | 25.101(c)(5)(D) | This project is reimbursable by TXI. | 208559 | 0 | 208559 |  |  | 66 | 208559 | 0 | 361597.62
04T64097 ME/MM | Temple Sw. Sta.-Temple S.-Belton 138 kV: Elevated temperature | Bell County | Replace selected existing wood H-frames with taller ones to allow the line to be operated at an elevated temperature. | 2005-03-02 | 2005-04-12 |  | 340000 |  |  |  | 0 | 138 | na | 10.98 | 795 kcmil ACSS & 795 kcmil ACSR | Steel Towers and Wood H-Frames | 100 | 10.98 | na | na | 25.101(c)(5)(B) |  | 340000 | 0 | 340000 |  |  | 67 | 340000 | 0 | 361597.62
04T65173 ME/MM | Mt. Creek-Norwood 138 kV: Elevated temperature | City of DallasDallas, Dallas County | Replace selected existing poles with taller ones to allow the line to be operated at an elevated temperature. | 2005-06-13 | 2005-07-08 |  | 115000 |  |  |  | 0 | 138 | na | 8.6 | 795 kcmil ACSS | Steel Towers and Steel Poles | 100 | 7.82 | na | na | 25.101(c)(5)(B) |  | 115000 | 0 | 115000 |  |  | 68 | 115000 | 0 | 361597.62
04T62105 ME/MM | Saginaw-Roanoke 138 kV: Elevated temperature | City of Fort Worth, City of Haltom City and City of Keller, Tarrant County and Denton County | Replace selected existing poles with taller ones to allow the line to be operated at an elevated temperature. | 2005-05-18 | 2005-06-28 |  | 198000 |  |  |  | 0 | 138 | na | 22.58 | 795 kcmil ACSR & 1033 kcmil ACSR | Steel Towers and Steel Poles | 75 | 22.58 | na | na | 25.101(c)(5)(B) |  | 198000 | 0 | 198000 |  |  | 69 | 198000 | 0 | 361597.62
04T62106 ME/MM | Saginaw-Euless 138 kV: Elevated temperature | City of Fort Worth, City of Haltom City, City of Bedford and City of Euless, Tarrant County | Replace selected existing poles with taller ones to allow the line to be operated at an elevated temperature. | 2005-06-06 | 2005-07-29 |  | 504000 |  |  |  | 0 | 138 | na | 16.19 | 795 kcmil ACSR | Steel Towers and Steel Poles | 100 | 15.03 | na | na | 25.101(c)(5)(B) |  | 504000 | 0 | 504000 |  |  | 70 | 504000 | 0 | 361597.62
04T64117 TW/RC | Temple Switch - Rogers 138 kV Line Rebuild | Bell County | Rebuild the 12.86 mile Temple Switch - Rogers 138kV line section with single 1929.9 kcmil ACSS/TW conductor. | 2005-02-23 | 2005-12-01 |  | 5964700 |  |  |  | 0 | 138 | na | 12.86 | 1926.9 kcmil ACSS/TW | Steel Poles & Steel H-Frames | 85 | 12.86 | na | na | 25.101(c)(5)(B) |  | 5964700 | 0 | 5964700 |  |  | 71 | 5964700 | 0 | 361597.62
05T64040 SEI/BW | West Waco-Belton 138kV: South Bosque River | City of Waco,McLennan County | Remove three wood H-frames and install two concrete H-frames to prevent failure of wood H-frame being encroached by South Bosque River. | 2005-01-24 | 2005-01-26 | 2005-01-26 | 75416 | 108404 |  |  | 100 | 138 | na | 0.41 | 795 kcmil ACSR | Wood H-Frame | 100 | 0.41 | na | na | 25.101(c)(3) | Final costs accumulating. | 108404 | 0 | 108404 |  |  | 72 | 75416 | 32988 | 394585.62
04T62069 JB/EH | Keller Substation - Roanoke Jct 138kV: Rebuild | City of Keller,Tarrant County | Rebuild 1.4 miles of existing double circuit 1033 kcmil ACSR conductor on steel poles and steel towers with bundled 1033 kcmil ACSR on steel poles. | 2005-04-01 | 2005-05-15 |  | 1350000 |  |  |  | 0 | 138 | na | 2.8 | 1033 kcmil ACSR Bundled | Steel Poles | 100 | 1.4 | na | na | 25.101(c)(5)(B) | This line section is only 1.4 miles of the 16.5 mile complete line from Keller Substation to Euless Substation. This filing is for the 1.4 mile section only; all other line sections will be filed separately. Interim report filed 01/31/2005. | 1350000 | 0 | 1350000 |  |  | 73 | 1350000 | 0 | 394585.62
05T61052 05T61051 WB/BM | North Main Duval 69 kV: Relocate Transmission Facilities for Tarrant County College | City of Fort Worth, Tarrant County | Tarrant County College has purchased a portion of the existing TXU property surrounding the North Main SES, North Main Substation and Heritage Substation. Accordingly, the North Main SES - Duval 69 kV line must removed out of the land purchased from TXU. This work will include removing four existing steel towers and erecting two new self supporting steel poles. The North Main East and West circuits are currently tied together but will be dead-ended on a common structure with the North Main SES - Denton 69 kV line. | 2005-03-15 | 2005-05-15 |  | 541768 |  |  |  | 0 | 69 | na | 0.1 | 795 kcmil ACSR | Steel Poles | 50 | 0.3 | 50 | 0.1 | 25.101(c)(5)(E) | These projects are reimbursable. Interim report filed 01/31/2005. | 541768 | 0 | 541768 |  |  | 74 | 541768 | 0 | 394585.62
05T63025 MMW | Wink-North Andrews 138 kV | Winkler County | A portion of the Wink-North Andrews 138 kV Line crosses an area that is subsiding. These areas have been known to collapse instantaneouly and without notice. If the area were to collapse, an extended outage on the 138 kV line would occur. In order to resolve this problem, it is proposed to rebuild a portion of the Wink-Keystone East 69 kV Line as double circuit. The portion of the Wink-North Andrews 138 kV Line that is in jeapordy would be placed on the second position. | 2005-04-01 | 2005-05-15 |  | 350000 |  |  |  | 0 | 138 and 69 | 138 and 69 | 8.64 | Single 556.5 kcmil ACSR (existing 138 kV) Single 795 kcmil ACSR (proposed 138 kV) Single 1/0 ACSR (existing 69 kV) Single 336.4 kcmil ACSR (proposed 69 kV) | Concrete Poles | Not Defined | 4.32 (69 kV) 3.12 (138 kV) | na | na | 25.101(c)(5)(E) |  | 350000 | 0 | 350000 |  |  | 75
04T64112 WB/RG | Lake Creek-Temple Switch 138 kV Line Mods to cut in Temple Pecan Creek | Bell County | Cut the new Temple Pecan Creek Substation into the existing Lake Creek-Temple Switch 138 kV line utilizing steel structures with single 1590 kcmil ACSR conductor. The length of line modified is approximately 0.25 miles. | 2005-08-15 | 2005-06-01 |  | 722137 |  |  |  | 0 | 138 | na | 0.25 | 1590 kcmil ACSR | Steel Poles | 100 | 0.25 | na | na | 25.101(c)(5)(A) |  | 722137 | 0 | 722137 |  |  | 76
04T64113 WB/RG | Lake Creek-Temple Switch 345 kV Line Mods to cut in Temple Pecan Creek | Bell County | Cut the new Temple Pecan Creek Substation into the existing Lake Creek-Temple Switch 345 kV line utilizing steel structures with 2-bundle 1590 kcmil ACSR conductor. The length of line modified is approximately 0.25 miles. | 2005-08-15 | 2005-12-31 |  | 2082265 |  |  |  | 0 | 345 | na | 0.5 | 2-bundle 1590 kcmil ACSR | Steel Poles | 170 | 0.25 | na | na | 25.101(c)(5)(A) |  | 2082265 | 0 | 2082265 |  |  | 77
04T64114 WB/RG | West Waco-Belton: 138 kV Line Extensions into Temple Elm Creek | City of Temple, Bell County | This project has two parts: 1.) Rebuild 0.5 miles of the existing Temple Switch-North Temple 138 kV line between Temple Elm Creek and North Temple using new double-circuit structures with single 1590 ACSR conductor. The existing Temple Switch-North Temple circuit will be re-routed into the new Temple Elm Creek Substation, thus creating the Temple Switch-Temple Elm Creek 138 kV circuit and two circuits between North Temple and Temple Elm Creek. 2.) Cut the existing W. Waco to Belton 138 kV line (McGregor Phillips - North Temple Section) just east of the North Temple Substation and extend it into Temple Elm Creek by constructing 0.5 miles of 138 kV line using new double circuit structures with single 1590 ACSR, with one circuit in place. This will create a circuit from W Waco to Temple Elm Creek. | 2005-08-15 | 2005-06-01 |  | 2242911 |  |  |  | 0 | 138 | na | 1.5 | 1590 kcmil ACSR | Steel Poles | 100 | 0.5 | na | na | 25.101(c)(5)(A) 25.101(c)(5)(B) |  | 2242911 | 0 | 2242911 |  |  | 78
04T64120 JFO | Southeast Tyler-Stryker 138 kV: Install CCEC Walnut Grove Substation POI. | Smith County | TXU Electric Delivery and Cherokee County Electric Cooperative are parties to an Interconnection Agreement under which TXU Electric Delivery is to design, procure the equipment, and construct the interconnection switch structure in order to establish the proposed CCEC Walnut Grove Substation. | 2005-04-01 | 2005-05-15 |  | 219000 |  |  |  | 0 | 138 | na | 0.01 | 795 kcmil ACSR Bundled | Steel Poles | 100 | na | na | na | 25.101(c)(5)(A) |  | 219000 | 0 | 219000 |  |  | 79
05T65108 JFO | West Plano-Payne 138 kV: Install Texas Instruments POI | City of Richardson,Dallas County | This project is to route the south circuit of the West Plano - Allen Switch 138 kV Line into the new TI Point of Delivery. | 2005-04-01 | 2005-05-30 |  | 225000 |  |  |  | 0 | 138 | na | 0.01 | 926 kcmil ACSS Bundled | Steel Poles | 100 | na | na | na | 25.101(c)(5)(A) |  | 225000 | 0 | 225000 |  |  | 80
04T65171 ME/MM | Allen Sw. Sta. - W. Plano | City of Plano, Collin County | Raise selected existing towers to allow the line to be operated at an elevated temperature. | 2005-03-01 | 2005-04-05 |  | 267000 |  |  |  | 0 | 138 | na | 12.4 | 795 kcmil ACSR | Lattice Towers and Steel Poles | 100 | 6.2 | na | na | 25.101(C)(5)(B) |  | 267000 | 0 | 267000 |  |  | 81
04T65180 ME/MM | Plano Shiloh-E. Richardson 138 kV: Elevated temperature | City of Richardson, Dallas County and Collin County | Raise selected existing towers to allow the line to be operated at an elevated temperature. | 2005-03-14 | 2005-04-22 |  | 455000 |  |  |  | 0 | 138 | na | 5.79 | 795 kcmil ACSR | Steel Towers and Steel Poles | 50 & 150 | 5.79 | na | na | 25.101(C)(5)(B) |  | 455000 | 0 | 455000 |  |  | 82
05T64074 JLA | Elkton-Jacksonville 138 kV Line: Provide 138 KV POI for TXU's Flint Substation | Smith County | Deadend existing conductors on Flint Substation deadend. | 2005-04-01 | 2005-06-01 |  | 61000 |  |  |  | 0 | 138 | N/A | 0.1 | 336.4 kcmil ACSR Bundled | Wood H-Frame | 75 | 0.1 | N/A | N/A | 25.101(c)(5)(A) | INTERIM PROJECT FILED MARCH 4, 2005. | 61000 | 0 | 61000 |  |  | 83
05T65158 MM | Greenville Ave.-800/900 Network 138 kV | City of Dallas, Dallas County | Reconfigure the existing Greenville Ave.-Flynn St.-800/900 Network 138 kV Line due to decommissioning the Flynn St. Terminal. In the fall of 2005, the Flynn St. 138 kV overhead to underground terminal will be decommissioned. The existing 138 kV circuit serving this terminal will be reconfigured such that it will bypass the terminal, creating the Greenville Ave.-800/900 Network 138 kV circuit. A new 138 kV overhead to underground terminal will be established at the 800/900 Network Station. New right-of-way will be required and has been obtained through a permit from the Texas Department of Transportation. | 2005-09-15 | 2005-12-30 |  | 276601 |  |  |  | 0 | 138 | N/A | 0.24 | 1233.6 kcmil ACSS/TW | Steel Poles | na | na | na | na | 25.101(c)(5)(B) | This portion of the line will be placed on TXDOT right-of-way. Right-of-way width is not defined. INTERIM PROJECT FILED MARCH 4, 2005. | 276601 | 0 | 276601 |  |  | 84
04T61031 BW/BM | Pflugerville-Gilleleand 138 kV:Relocate for SH 130 near Cameron Rd | Travis County | The TTA has requested that a section of the PFlugerville-Gilleland 138 kV line be relocated to accomodate the SH-130 toll road. Eight existing 138 kV double circuit structures will have to be removed ands Six new structures will have to be added to accomodate the new roadway. These structures are currently supporting two circuits of 1590 kcmil ACSR. TXU has agreed to relocate the 138 kV line within the SH-130 ROW with the provisions that if the line has to ever be relocated again for the TTA that the TTA will pick up all expenses associated with this relocation. The cost of the project is to be totally refunded by Lone Star Infrastructure. | 2005-04-01 | 2005-05-15 |  | 973273.04 |  |  |  | 0 | 138 | na | 0.48 | 1590 kcmil ACSR | Steel Poles | 100 | 0.67 | 70 | 0.48 | 25.101(c)(5)(F) | INTERIM PROJECT FILED MARCH 4, 2005. | 973273.04 | 0 | 973273.04 |  |  | 85
| CCN APPLICATIONS - APPROVED | [21 empty] | 0 | 0 | 0 |  |  | 86
04T65188 MM | Paris-Valley 345 kV: Add Second Circuit | Fannin County and Lamar County | Add a second 345 kV circuit to existing double circuit steel towers. | 2006-01-03 | 2006-03-30 |  | 11717149 |  |  |  | 0 | 345 | N/A | 46 | 1590 kcmil ACSR Bundles | Steel Towers | 200 | 46 | N/A | N/A | 22665 | INTERIM PROJECT FILED MARCH 4, 2005. | 11717149 | 0 | 11717149 |  |  | 87
04T65189 MM | Valley-Valley Jct. 345 kV: Add Second Circuit | Fannin County and Collin County | Add a second 345 kV circuit to existing double circuit steel towers. | 2006-03-31 | 2006-05-01 |  | 5008417 |  |  |  | 0 | 345 | N/A | 24.53 | 959.6 kcmil ACSS/TW Bundled | Steel Towers | 170 | 24.53 | N/A | N/A | 22665 | INTERIM PROJECT FILED MARCH 4, 2005. | 5008417 | 0 | 5008417 |  |  | 88
04T65190 MM | Valley Jct.-Anna 345 kV: Add Second Circuit | Collin County | Add a second 345 kV circuit to existing double circuit steel poles. | 2005-05-02 | 2006-06-15 |  | 8286852 |  |  |  | 0 | 345 | N/A | 19.9 | 1590 kcmil ACSR Bundled | Steel Poles | 160 | 19.9 | N/A | N/A | 22665 | INTERIM PROJECT FILED MARCH 4, 2005. | 8286852 | 0 | 8286852 |  |  | 89
04T65160 JE/TW | Cedar Hill-DeSoto 138 kV 2nd Circuit | City of DeSoto, City of Glenn Heights, and the City of Cedar Hill, Dallas County | Remove existing single-circuit 138 kV line on wood H-frames and replace with new double circuit 138 kV line on steel or concrete poles | 2006-01-01 | 2006-05-15 |  | 4532000 |  |  |  | 0 | 138 | na | 6.2 | 1590 kcmil ACSR | Steel Poles and Concrete Poles | 75 | 6.2 | na | na | 23604 | Notice of Approval 04/11/01. | 4532000 | 0 | 4532000 |  |  | 90 | 4532000 | 0 | 394585.62
04T65159 DRC | Watermill - Lancaster 138 kV | Dallas County | Construct approximately 3.00 miles of 138 kV transmission line from Watermill Switching Station to line section that travels north to Lancaster Substation to vacate 2nd position on 345 kV towers | 2004-12-01 | 2005-05-15 |  | 836190 | 1375000 |  |  | 75 | na | 138 | 3 | 1590 kcmil ACSR | Concrete Poles | 100 | 3 | na | na | 25321 | Final Order issued 12/09/02. | 1375000 | 0 | 1375000 |  |  | 91 | 1375000 | 0 | 394585.62
03T65046 04T65237 TW/RC | Collin - Renner 138 kV | City of Plano and the City of Frisco, Collin County | Replace single circuit wood H-frame 138 kV line with single steel pole double circuit 138 kV line from Collin plant to Allen Junction to Renner Sw. Station | 2003-02-10 | 2005-05-15 |  | 12414319 | 12414319 |  |  | 80 | 138 | na | 27.8 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 13.9 | na | na | 25179, 25.101(c)(5)(B) | Final Order issued 11/25/02. Will be completed in sections. | 12414319 | 0 | 12414319 |  |  | 92 | 12414319 | 0 | 394585.62
03T65131 DRC | Watermill - W. Levee 345 kV: Add Second 345 kV Circuit | City of Dallas,Dallas County | Add the second 345 kV circuit to existing structures from Watermill Switching Station to W. Levee Switching Substation. In addition, make the necessary line changes to connect the new Sargent Road Substation to the transmission line. | 2003-10-01 | 2005-04-15 |  | 3975000 | 3975000 |  |  | 91 | 345 | na | 9 | 1590 kcmil ACSR Bundled | Steel Poles | 100 | 9 | na | na | 25.101(b)(3) | CCN previously approved and one circuit already constructed. Interim Report filed 6/27/2003. Project cannot be completed at this time due to railroad crossing mitigation. | 3975000 | 0 | 3975000 |  |  | 93 | 3975000 | 0 | 394585.62
ABCD1 | Carrollton Country Club 138 kV | City of Addison and the City of Carrollton, Dallas County | Construct 1.32 miles 138 kV double circuit on single poles to Carrollton Countly Club Substation | 2005-09-30 | 2006-05-15 |  | 3653273 |  |  |  | 0 | na | 138 | 2.64 | 1590 kcmil ACSR | Steel and/or Concrete Poles | 100 | 1.32 | na | na | 27030 | Application filed 11/27/02. Final Order issued 08/07/03. | 3653273 | 0 | 3653273 |  |  | 94 | 3653273 | 0 | 394585.62
04T64042 BW/RG | Copperas Cove-Ding Dong 138 kV | Bell County, Coryell County | Construct 15.7 miles 138 kV single circuit single pole from TXU Electric Delivery Copperas Cove Substation to BEPC's Ding Dong Substation | 2005-09-01 | 2005-12-31 |  | 7145776 |  |  |  | 0 | na | 138 | 15.7 | 795 kcmil ACSS | Steel and/or Concrete Poles | na | na | 70/100 | 15.7 | 27179 | Application filed 12/31/02. Application approved 01/29/2004. | 7145776 | 0 | 7145776 |  |  | 95 | 7145776 | 0 | 394585.62
04T64091WB/RG | Temple Pecan Creek Switch - Temple Elm Creek Switch 138 kV | Bell County | Construct 4.7 miles 138 kV double circuit single pole from new Temple Pecan Creek Switching Station to the new Temple Elm Creek Switching Station. | 2005-05-01 | 2006-05-15 |  | 4788194 | 5471491 |  |  | 0 | na | 138 | 9.4 | 1590 kcmil ACSR | Steel Poles | na | na | 70 | 4.7 | 27173 | Application filed 12/27/02. Application approved 01/15/2004. | 5471491 | 0 | 5471491 |  |  | 96 | #N/A | 683297 | 1077882.62 | 683297 | 4788194 | 5471491
ABCD6 | Pleasant Valley - Iowa Park Tap 69 kV | Wichita County | Construct 4.5 miles 69 kV single circuit single pole on 138 kV structures from Pleasant Valley to Iowa Park Tap | 2006-01-01 | 2006-05-31 |  | 2857000 |  |  |  | 0 | na | 69 | 4.5 | 795 kcmil ACSR | Steel and/or Concrete Poles | na | na | 30 | 4.5 | 29768 | Application approved 09/28/2004. | 2857000 | 0 | 2857000 |  |  | 97 | 2857000 | 0 | 1077882.62
04T65208 DRC | Watermill-Cedar Hill 345 kV: Add second circuit | City of Lancaster, Dallas County | Construct second circuit to existing 345 kV structures. New structures added at both ends of the project. New conductor to be 959.6 kcmil ACSS/TW bundles for operation at elevated temperature. | 2005-02-16 | 2005-05-15 |  | 4630000 |  |  |  | 0 | 345 | na | 17.3 | 959.6 kcmil ACSS/TW Bundled | Steel Towers | 150 | 17.3 | na | na | 25.101(c)(5)(B) | Interim Report filed 6/23/04. CCN previously approved and one circuit already constructed. | 4630000 | 0 | 4630000 |  |  | 98 | 4630000 | 0 | 1077882.62
| CCN APPLICATIONS - PENDING | [21 empty] | 0 | 0 | 0 |  |  | 99
ABCD7 | Jacksboro - W. Denton 345 kV | Wise, Jacksboro, and Denton Counties | Construct 66.4 miles of 345 kV double-circuit line from Jacksboro Switch to West Denton Switch with 1 circuit installed initially and 2nd circuit to be installed later as needed. | 2006-02-01 | 2006-12-15 |  | 62023000 |  |  |  | 0 | na | 345 | 66.4 | 1590 kcmil ACSR Bundled | Steel Towers | na | na | 160 | 66.4 | 30168 |  | 62023000 | 0 | 62023000 |  |  | 100 | 62023000 | 0 | 1077882.62
| COMPLETED PROJECTS REMOVED FROM 01/15/2005 REPORT. | [21 empty] | 0 | 0 | 0 |  |  | 101 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | 102
[23 empty] | 0 | 0 | 0 |  |  | 103 | #N/A | #N/A | #N/A
| 14 | [5 empty] | 32886605.04
107
108
109
110
111
112
03T63053 ALK | Sun - Cielo 138 kV: Construct tie to Cielo Wind Power transmission line. | Scurry County | Install one span of 1033.5 kcmil ACSR conductor to connect the Cielo Wind Power 138 kV Transmission Line to the TXU Electric Delivery system at the Sun Substation. | 2003-12-15 | 2003-12-22 | 2003-12-22 | 7773 | 7773 | 6059 | -22.05% | 100 | na | 138 | 0.05 | 1033.5 kcmil ACSR | Wood Poles | na | na | 75 | 0.05 | 25.101(c)(5)(A) | This new span will utilize existing TXU Electric Delivery right of way. | [5 empty] | 113
03T65096 03T65097 TW | Plano Tennyson 138 kV Loop Line | City of Plano, City of The Colony,and the City of Carrollton, Collin County and Denton County | Construct approx. 5.70 miles of 138 kV transmission line from existing NW Carrollton-Collin SES 138 kV Transmission Line to the existing Plano Tennyson Switching Station | 2003-08-18 | 2003-12-30 | 2003-12-30 | 8967000 | 7204966 | 6514316 | -10% | 100 | na | 138 | 11.4 | 1590 kcmil ACSR | Steel Poles | 170 | 5.7 | 70 | 5.7 | 21664 | Final Order 08/06/01. | [5 empty] | 114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
|  | NEW PROJECTS: | 18829245
6
0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 6538590 | 44680 | 340032014.04 | 340076694.04
[24 empty] | 1 | 97 | 98 | Project Count
[24 empty] | Completed | Active | Total
Note on A95: aboling: THIS PROJECT NUMBER ENTERED BY PUC STAFF TO FACILITATE TROUBLESHOOTING OF THIS REPORT.
Note on A98: aboling: THIS PROJECT NUMBER ENTERED BY PUC STAFF TO FACILITATE TROUBLESHOOTING OF THIS REPORT.
Note on A101: aboling: THIS PROJECT NUMBER ENTERED BY PUC STAFF TO FACILITATE TROUBLESHOOTING OF THIS REPORT.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H8: Allen Steven Boling: VALUE ADDED BY PUC STAFF.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AD3: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD31: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD60: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD76: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD77: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD78: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD79: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD80: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD81: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD82: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD83: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD84: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD85: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD86: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD88: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD89: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD90: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AD103: aboling: FORMULAS DELETED DUE TO PROJECT NUMBER CHANGE.
Note on AE3: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE31: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE60: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE76: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE77: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE78: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE79: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE80: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE81: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE82: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE83: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE84: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE85: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE86: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE88: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE89: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE90: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AE97: Allen Steven Boling: PROJECT NUMBER CHANGED AT SAME TIME COST ESTIMATE WAS REVISED. THIS IS A ONE TIME MANUAL ENTRY !!
Note on AE103: aboling: FORMULAS DELETED DUE TO PROJECT NUMBER CHANGE.
Note on AF3: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF31: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF60: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF76: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF77: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF78: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF79: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF80: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF81: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF82: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF83: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF84: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF85: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF86: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF88: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF89: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF90: aboling: FORMULAS DELETED TO ALLOW NEW PROJECT.
Note on AF103: aboling: FORMULAS DELETED DUE TO PROJECT NUMBER CHANGE.