## SUMMARY
Revised: | 2008-03-28
MONTHLY ACTIVITY AT A GLANCE
for
FEBRUARY 2008
TRANSMISSION PROJECTS
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O
UTILITY | TOTAL PROJECTS REPORTED =Utility!AA102 | ESTIMATED COST FOR ALL REPORTED PROJECTS =Utility!AA100 | NEW PROJECTS COUNT THIS MONTH Manual Entry | 1st ESTIMATE COST FOR NEW PROJECTS Manual Entry | COMPLETED PROJECTS COUNT THIS MONTH =Utility!Y102 | COMPLETED PROJECTS (FINAL ACTUAL COSTS) =Utility!X100 | COMPLETED PROJECTS (FINAL ESTIMATED COSTS) =Utility!Y100 | ONGOING PROJECT COUNT = B - F | ONGOING PROJECT COST ESTIMATE (THIS MONTH) = C - H | ONGOING PROJECT COST ESTIMATE (FROM LAST MONTH) Linked or Manual | NET ONGOING PROJECT CHANGE FROM LAST MONTH = J - K | DIFFERENCE: NEW PROJECTS LESS COMPLETED PROJECTS = E - H | CALCULATED COST ADJUSTMENT TO EXISTING PROJECTS = L - M | EXPLANATION OR COMMENT
AEPC | 39 | 288628973 | 0 | 0 | 0 | 0 | 0 | 39 | 288628973 | 288628973 | 0 | 0 | 0
AEPN | 11 | 60305194 | 0 | 0 | 1 | 4824012 | 5148800 | 10 | 55156394 | 60305194 | -5148800 | -5148800 | 0
BEPC | 23 | 131848705 | 0 | 0 | 0 | 0 | 0 | 23 | 131848705 | 131848705 | 0 | 0 | 0
CNP | 19 | 127189000 | 1 | 1603000 | 1 | 10183215.57 | 11200000 | 18 | 115989000 | 124056000 | -8067000 | -9597000 | 1530000 | Cost Revisions 5 Projects
DSEC | 2 | 5095000 | 0 | 0 | 0 | 0 | 0 | 2 | 5095000 | 5095000 | 0 | 0 | 0
EGSI | 7 | 32503438 | 0 | 0 | 0 | 0 | 0 | 7 | 32503438 | 32503438 | 0 | 0 | 0
EPE | 6 | 13836707 | 0 | 0 | 0 | 0 | 0 | 6 | 13836707 | 13836707 | 0 | 0 | 0
FEC | 2 | 4721500 | 0 | 0 | 0 | 0 | 0 | 2 | 4721500 | 4721500 | 0 | 0 | 0
GSEC | 1 | 3415000 | 0 | 0 | 0 | 0 | 0 | 1 | 3415000 | 3415000 | 0 | 0 | 0
KELSON | 1 | 268250000 | 0 | 0 | 0 | 0 | 0 | 1 | 268250000 | 268250000 | 0 | 0 | 0
LCRA | 15 | 251398914 | 2 | 1381510 | 0 | 0 | 0 | 15 | 251398914 | 250087555 | 1311359 | 1381510 | -70151 | Cost Revisions 2 Projects
MVEC | 7 | 16184500 | 0 | 0 | 0 | 0 | 0 | 7 | 16184500 | 16184500 | 0 | 0 | 0
LEA E.C. |  |  | 0 | 0
PEC | 2 | 6835000 | 0 | 0 | 0 | 0 | 0 | 2 | 6835000 | 6835000 | 0 | 0 | 0
RCEC | 1 | 5689837 | 0 | 0 | 0 | 0 | 0 | 1 | 5689837 | 5689837 | 0 | 0 | 0
SHECO | 1 | 981531 | 1 | 981531 | 0 | 0 | 0 | 1 | 981531 | 0 | 981531 | 981531 | 0 | First time to report
SPS | 4 | 27132831 | 0 | 0 | 0 | 0 | 0 | 4 | 27132831 | 27132831 | 0 | 0 | 0
STEC | 11 | 68503412 | 0 | 0 | 0 | 0 | 0 | 11 | 68503412 | 68503412 | 0 | 0 | 0
SULP | 1 | 39000000 | 0 | 0 | 0 | 0 | 0 | 1 | 39000000 | 39000000 | 0 | 0 | 0
SWEPCO | 3 | 21838942 | 1 | 750377 | 0 | 0 | 0 | 3 | 21838942 | 21088565 | 750377 | 750377 | 0
TNMP | 3 | 12266731 | 1 | 8800000 | 0 | 0 | 0 | 3 | 12266731 | 3466731 | 8800000 | 8800000 | 0
TVEC | 3 | 9954063 | 0 | 0 | 0 | 0 | 0 | 3 | 9954063 | 14000000 | -4045937 | 0 | -4045937 | Cost Rev 1 Project
TXU | 110 | 239856419.09 | 5 | 854080 | 9 | 27956105 | 15889212 | 101 | 223967207.09 | 239002339.09 | -15035132 | -15035132 | 0 |  |  | 0 | (From TXU Sheet)
UPSHUR | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NOT REPORTING
WCEC | 2 | 7869111 | 0 | 0 | 0 | 0 | 0 | 2 | 7869111 | 7869111 | 0 | 0 | 0 |  | Less: | 0 | (From Calc Cost Adj)
NEW3 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEW4 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[15 empty] | = | 0 | (Difference)
TOTAL | 274 | 1643304808.09 | 11 | 14370498 | 11 | 42963332.57 | 32238012 | 263 | 1611066796.09 | 1631520398.09 | -20453602 | -17867514 | -2586088
|  | Ongoing Project Count Check: | 263 | Correct |  |  | LAST MONTH ONGOING COUNT: | 263
AEPC | American Electric Power TNC |  |  |  | LEA E.C.* | Lea County Electric Cooperative
AEPN | American Electric Power TCC |  |  |  | PEC | Pedernales Electric Cooperative
BEPC | Brazos Electric Power Cooperative |  |  |  | RCEC | Rayburn Country Electric Cooperative
CNP | Centerpoint Energy |  |  |  | SHECO | Sam Houston Electric Cooperative
DSEC | Deaf Smith Electric Cooperative |  |  |  | SPS | Southwestern Public Service Company
EGSI | Entergy Texas, Inc. |  |  |  | STEC | South Texas Electric Cooperative
EPE | El Paso Electric |  |  |  | SULP | Sharyland Utilities, LP
FEC | Farmers Electric Cooperative |  |  |  | SWEPCO | Southwestern Electric Power Company
GSEC | Golden Spread Electric Cooperative |  |  |  | TNMP | Texas-New Mexico Power Company
KELSON | Kelson Electric Transmission, LLC |  |  |  | TVEC | Trinity Valley Electric Cooperative
LCRA | LCRA TCC |  |  |  | TXU | ONCOR Electric Transmission Company
MVEC | Magic Valley Electric Cooperative |  |  |  | UPSHUR* | Upshur County Electric Cooperative
[5 empty] | WCEC | Wood Country Electric Cooperative
* Not Currently Reportiing
Note on A11: aboling: FORMERLY CPL.
Note on A12: aboling: FORMERLY WTU
Note on A14: aboling: FORMERLY CPE.
Note on A16: Allen Steven Boling: ENTERGY TEXAS, INCORPORATED
Note on A18: Allen Steven Boling: Farmer's Electric Cooperative AKA Concho Valley EC. CVEC
Note on A19: Allen Steven Boling: GOLDEN SPREAD ELECTRIC COOPERATIVE
Note on A20: Allen Steven Boling: KELSON TRANSMISSION COMPANY, LLC
Note on A25: Allen Steven Boling: RAYBURN COUNTRY ELECTRIC COOPERATIVE, INC.
Note on A29: aboling: SHARYLAND UTILITIES
Note on A33: aboling: "Oncor" changed to TXU Electric Delivery Company.
Note on A35: Allen Steven Boling: Wood County Electric Cooperative
Note on F10: aboling: A COMPLETE PROJECT IS DEFINED AS ONE FOR WHICH THE CONSTRUCTION IS COMPLETE AND THE FINAL ACTUAL PROJECT COST HAS BEEN ENTERED.
Note on I10: aboling: ACTIVE PROJECTS INCLUDE NEW PROJECTS BUT NOT COMPLETED PROJECTS.

## AEPC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
22169662 | Falcon-Lopeno 138 kV Line Reconductor | Starr & Zapata Counties, Texas | Reconductor and rebuild approximately 10 miles of existing 138kV transmission line from Falcon Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2001-12-15 | 2002-02-15 | 2002-02-21 |  | 2140875 |  |  | 100 | 138 | 138 | 10 | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 10 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified service area. | 2140875 | 0 | 2140875 |  |  | 2140875 | 0 | 0
22169585 | Garza- Falcon 138 kV Line Reconductor | Starr County, Texas | Reconductor and rebuild approximately 27.3 miles of existing 138kV transmission line from Garza Substation to Falcon Substation. The old line is 336 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM aluminum conductor on steel poles. | 2002-03-10 | 2002-10-10 | 2002-10-10 |  | 5577000 |  |  | 100 | 138 | 138 | 27.3 | 795 MCM & 7#8 Alumoweld Static | Steel Single Poles | Ceterline Defined | 27.3 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | This line is located in MEC (Medina Electric Coop) single certified service area. | 5577000 | 0 | 5577000 |  |  | 5577000 | 0 | 0
22169764 | Lopeno-Zapata 138 kV Line Reconductor | Zapata County, Texas | Reconductor and rebuild approximately 20.3 miles of existing 138kV transmission line from Zapata Substation to Lopeno Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-02-22 | 2003-01-30 | 2003-02-01 |  | 4168000 |  |  | 100 | 138 | 138 | 20.3 | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 20.3 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified service area. | 4168000 | 0 | 4168000 |  |  | 4168000 | 0 | 0
22169796 | Rio Bravo-Zapata 138 kV Line Reconductor | Zapata & Webb Counties, Texas | Reconductor and rebuild approximately 30.8 miles of existing 138kV transmission line from Zapata Substation to Rio Bravo Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-05-15 | 2003-04-15 | 2003-05-15 |  | 6308000 |  |  | 100 | 138 | 138 | 30.8 | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Ceterline Defined | 30.8 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified & TCC single certified service areas. | 6308000 | 0 | 6308000 |  |  | 6308000 | 0 | 0
22169830 | Wormser-Rio Bravo 138kV Reconductor | Webb County, Texas | Reconductor and rebuild approximately 9.6 miles of existing 138kV transmission line from Rio Bravo Substation to Wormser Substation. The old line is 336.4 MCM Aluminum conductor on wood H frame structures and will be reconductored with 795 MCM ACSR conductors on steel poles. | 2002-06-15 | 2003-05-15 | 2003-11-19 |  | 2201000 |  |  | 100 | 138 | 138 | 9.6 | 795 MCM ACSR & 7#8 Alumoweld | Steel Single Poles | Center line Defined | 29.6 |  |  | Sub Rule 25.101 (c) (2) (C) (ii) | The line is located in MEC single certified & TCC single certified service areas. | 2201000 | 0 | 2201000 |  |  | 2201000 | 0 | 0
40389465 | N McAllen - W. McAllen 138kV at FM 2220 | Hidalgo County, Texas | Relocate 16 structures for road improvement | 2004-07-15 | 2004-10-01 |  |  | 418000 |  |  | 5 | 138 |  | 0.76 | 795 AAC 37 strand | Steel pole | Cenerline Defined | 0.76 |  |  | Sub Rule 25.101 (c) (5) (F) | Relocation located in public Right-Of-Way acquired by TXDot | 418000 | 0 | 418000 |  |  | 418000 | 0 | 0
40419748 | Rio Hondo to La Palma 138kV Rebuild | Cameron County, Texas | Rebuild approximately 10.1 miles of existing wood H-frame 138kV line. The old line is single 795 ACSR 27/7. The new line will be bundled 795 ACSS with OPGW on new steel single pole structures. | 2005-08-15 | 2005-12-31 | 2005-12-16 |  | 16510075 |  |  | 99 | 138 | 138 | 10.1 | Bundled 795 ACSS | Steel single pole | Centerline Defined | 10.1 |  |  | Pursuant to Subst. Rule 25.101 (c)(5) (B) |  | 16510075 | 0 | 16510075 |  |  | 16510075 | 0 | 0
40213325 | Airline / Laguna 69 kV Line - Rebuild Line | Corpus Christi, Nueces | Reconductor and rebuild approximately 6.4 miles of existing 69 kV transmission line from Airline Substation to Laguna Substation. The old line is 477 MCM ACSR on wooden H frame structures and will be reconductored with 795 MCM ACSR conductor on steel poles. | 2008-04-01 | 2008-06-30 |  |  | 4799103 |  |  |  | 69 | 69 | 6.4 | 795 ACSR | Steel Monopole | Centerline Defined (50%), Varied width of 15 ft - 45 ft (50%) | 6.4 |  |  | Sub Rule 25.101 (c)(5)(B) | Has section of line that crosses Oso Bay | 4799103 | 0 | 4799103 |  |  | 4799103 | 0 | 0
40213354 | Airline / Naval Base 69 kV Line - Rebuild Line | Corpus Christi, Nueces | Reconductor and rebuild approximately 7.96 miles of existing 69 kV transmission line from Airline Substation to Naval Base Substation. The old line is 477 MCM ACSR on wooden H frame structures and will be reconductored with 795 MCM ACSR conductor on steel poles. | 2008-07-15 | 2008-10-01 |  |  | 5950992 |  |  |  | 69 | 69 | 7.96 | 795 ACSR | Steel Monopole | Centerline Defined (75%), Varied width of 12 ft - 45 ft (25%) | 7.96 |  |  | Sub Rule 25.101 (c)(5)(B) | Has section of line that crosses Oso Bay | 5950992 | 0 | 5950992 |  |  | 5950992 | 0 | 0
25188819 | Uvalde-Hamilton Road Rebuild | Uvalde, Kinney, Val Verde | Rebuild 67.6 miles of the Uvalde-Hamilton Road transmission line | 2006-01-30 | 2007-05-14 |  |  | 34348277 |  |  | 99 | 138 | 138 | 67.6 | 795 ACSS | single steel pole | 50 minimum or undefined | 67.6 | 50 minimum or undefined |  | Sub.Rule 25.101(c)(5)(B) | The line is located in TCC and Rio Grande Electric Cooperatuve (RGEC) single certificated territories | 34348277 | 0 | 34348277 |  |  | 34348277 | 0 | 0
40616479 | Mustang/Port Aransas 69kV line (Flato Property) - reroute line | Nueces | Reroute 2.6 miles of 69kV line next to Highway 361 (Existing Easement Encroachment) | 2006-02-01 | 2007-05-01 |  |  | 3334427 |  |  | 100 | 69 | 69 | 2.6 | 795 MCM ACSS | Steel monopile | 60' | 2 | 60 | 2.6 | Sub. Rule 25.101 (c)(5)(E) | New ROW provided by landowner. | 3334427 | 0 | 3334427 |  |  | 3334427 | 0 | 0
40601028 | ExxonMobil KRGP 138 kV Hairpin | Kleberg | 138 kV Hairpin of the Falfurrias-Lon Hill transmission line into the ExxonMobil KRGP substation | 2006-01-31 | 2006-04-01 | 2006-03-03 |  | 593000 |  |  | 100 | 138 |  | 0.19 | 795 ACSR | single steel pole |  |  | 80 for each circuit of hairpin | 0.19 | Sub.Rule 25.101(c)(5)(A) | Consent provided | 593000 | 0 | 593000 |  |  | 593000 | 0 | 0
40654675 | Wormser to Sierra Vista 138 kV | Webb | Construct approximately 2.7 miles of 138kV transmission line using 795 kcmil ACSR on pre-stressed concrete or steel single pole structures | 2006-10-09 | 2007-04-26 | 2007-05-12 | 3241000 |  |  |  | 100 |  |  | 2.7 | 795 kcmil ACSR 26/7 | Centerline |  |  | 100 | 2.7 | 32172 | Line is located in TCC singly certificated territory | 3241000 | 0 | 3241000 |  |  | 3241000 | 0 | 0
40737207 | Laredo Plant to Zacate to Heights 69 kV to 138 kV Conversion | Laredo, Webb | Conversion of the existing 69 kV transmission line to 138 kV operation requiring some change out of insulators and some pole change outs. | 2006-07-17 | 2006-12-31 |  |  | 948200 |  |  |  | 69 | 138 | 8.4 | (1) 795,000 cm AAC 19 Comp | Double ckt. steel and Wood single pole | Centerline Defined | 4.2 | 30 | 0.08 | Sub.Rule 25.101(c)(5)(B) | Double Circuit Line with one side remaining 69kV and the other side converted to 138kV | 948200 | 0 | 948200 |  |  | 948200 | 0 | 0
4073529401 | Dupont SS Victoria / Gohlke 138 kV Line - Tie in Chocolate Bayou Substation | Victoria | 138 kV Double Circuit Hairpin from the Dupont SS Victoria / Gohlke Line to the Chocolate Bayou Substation | 2006-08-07 | 2006-12-15 | 2006-12-21 |  | 1279500 |  |  | 100 | 138 | 138 | 0.34 | 795 MCM ACSR | Steel Pole |  |  | 80 | 0.17 | Sub.Rule 25.101(c)(5)(A) | Consent and easements obtained | 1279500 | 0 | 1279500 |  |  | 1279500 | 0 | 0
40787097 | Milo Substation-Laredo 138kV Line (North Laredo to Laredo Plant 138kV Tie to Laredo VFT Station) | Laredo, Webb | Cut in 300 ft tap to Laredo VFT Station and rebuild replace (6) existing spans into Laredo Station with direct embed steel poles and 2 bundle 795,000cm ACSR Conductor | 2006-09-28 | 2006-12-31 | 2007-02-19 |  | 579000 |  |  |  | 138 | 138 | 0.52 | (2) 795,000 cm Drake ACSR | Single Circuit Steel Pole | Centerline Defined |  |  |  | Sub.Rules 25.101(c)(5) (A) and (B) | This line Section is located entirely on AEP TCC Property | 579000 | 0 | 579000 |  |  | 579000 | 0 | 0
40787138 | Bruni-Laredo 138kV Line (Falfurrias to Laredo Tie to Laredo VFT Station) | Laredo, Webb | Cut in 500 ft tap to Laredo VFT Station and rebuild replace (4) existing spans into Laredo Station with direct embed steel poles and 2 bundle 795,000cm ACSR Conductor | 2006-09-28 | 2006-12-31 | 2007-04-10 |  | 463000 |  |  |  | 138 | 138 | 0.55 | (2) 795,000 cm Drake ACSR | Single Circuit Steel Pole | Centerline Defined |  |  |  | Sub.Rules 25.101(c)(5) (A) and (B) | This line Section is located entirely on AEP TCC Property | 463000 | 0 | 463000 |  |  | 463000 | 0 | 0
40722975 | Laredo VFT-Nuevo Laredo CFE 230kV Line | Laredo, Webb | Conversion of (4) spans of the existing Laredo - Nuevo Laredo CFE 138kV transmission line to double circuit 230kV/138kV operation utilizing (2) bundle 795,000cm ACSS condutor and a new 300 ft termination into Laredo VFT Station. | 2006-09-28 | 2006-12-31 | 2007-03-26 |  | 1131000 |  |  |  | 138 | 230 | 0.76 | (2) 795,000 cm Drake ACSS | Double Circuit Steel Pole | 120' |  |  |  | Sub.Rule 25.101(c)(5) (A), (B), and (C) | Rebuild is completely on existing powerplant easement. | 1131000 | 0 | 1131000 |  |  | 1131000 | 0 | 0
40806045 | Laredo-Nuevo Laredo CFE 138kV Line | Laredo, Webb | Rebuild and Replacement of (3) spans of the existing Laredo - Nuevo Laredo CFE 138kV with 795,000cm ACSR and a new 350 ft termination into Laredo VFT Station. | 2006-09-28 | 2006-12-31 | 2007-05-15 |  | 311000 |  |  |  | 138 | 138 | 0.24 | (1) 795,000 cm Drake ACSR | Single Circuit Steel Pole | Centerline Defined |  |  |  | Sub.Rule 25.101(c)(5) (A) and (B) | Rebuild is completely on existing powerplant easement. | 311000 | 0 | 311000 |  |  | 311000 | 0 | 0
40737194a | Laredo Anna Street to Laredo Heights 69 kV to 138 kV Conversion | Laredo, Webb | Existing 69 kV single pole double circuit line is insulated for 138 kV operation. One circuit will be converted to 138 kV operation. Some substation work required. | 12/15//06 | 2006-12-31 |  |  | 200000 |  |  |  | 69 | 138 | 1.94 | (1) 795,000 cm AAC 19 Comp | Double ckt. steel and Wood single pole | Centerline Defined | 1.94 |  |  | Sub.Rule 25.101(c)(5)(B) | Double Circuit Line with one side remaining 69kV and the other side converted to 138kV | 200000 | 0 | 200000 |  |  | 200000 | 0 | 0
40636851a | Relocation of a section of the Whitepoint to Dupont 138 kV Line | Nueces | Relocation request results in 0.56 miles of new construction to the Whitepoint to Dupont 138 kV line. Requestor provided funding and easement. | 2006-10-13 | 2007-09-10 |  |  | 665200 |  |  |  | 138 | 138 | 0.56 | 795,000 ACSR | Double ckt. steel |  |  | 80 | 1.12 | Sub.Rule 25.101(c)(5)(D) | Requestor is providing funding and has provided the easement. | 665200 | 0 | 665200 |  |  | 665200 | 0 | 0
40636851 | Whitepoint to Dupont 138 kV Line cut-in to Cargo Substation | Nueces | Construct new 0.9 mile cut-in to new Cargo Substation from the Whitepoint to Dupont 138 kV line. | 2006-10-13 | 2007-10-15 |  |  | 795400 |  |  |  |  | 138 | 0.9 | 795,000 ACSR | Double ckt. Steel |  |  | 80 | 1.8 | Sub.Rule 25.101(c)(5)(A) | Consent and easements obtained | 795400 | 0 | 795400 |  |  | 795400 | 0 | 0
40487094 | San Miguel to Laredo Lobo 345 kV | Atascosa, La Salle, McMullen, Webb | Construct a new 345 kv line from San Miguel to a new Lobo Switching Station near Laredo, Texas | 2007-02-01 | 2010-04-30 |  | 72023400 | [5 empty] | 345 | 102-106 | 2-1590 kcmil ACSR | Double ckt. Capable Steel Monoploe |  |  | 150 | 102-106 | 33033 | Filed CCN on 9/12/2006. Joint line with STEC who has 40% of line cost. CNN approved 6/13/07 | 72023400 | 0 | 72023400 |  |  | 72023400 | 0 | 0
40779294 | Stewart Road 69/138 kV Double Circuit | Hidalgo | Construct approximately 2 miles of 69/138kV double circuit transmission line from new Stewart Road Switching Station to existing S. McAllen to La Palma 69 kV line | 2007-08-15 | 2007-12-15 | 2008-01-25 | 2394000 |  |  |  | 95 |  | 69/138 | 4 | 795 kcmil ACSS 26/7 | Concrete or steel single pole |  |  | 100 | 2 | 32857 | Filed CCN on 9/12/2006. Approved on December 5, 2006. | 2394000 | 0 | 2394000 |  |  | 2394000 | 0 | 0
4021289001 | Flato Property / Port Aransas 69 kV Line Rebuild | Port Aransas, Texas | Rebuild line from 4/0 to 795 MCM ACSS | 2006-11-20 | 2007-03-06 |  |  | 4500000 |  |  | 100 | 69 | 69 | 3.3 | 795 MCM ACSR | Steel Pole w/ concrete Butt Sections | Undefined Hwy Right of Way | 3.3 |  |  | Subst. Rule 25.101 (c)(5)(B) | Remains in Hwy Right of Way | 4500000 | 0 | 4500000 |  |  | 4500000 | 0 | 0
4049003701 | Laredo Variable Frequency Transformer (VFT) Station | Webb County, Laredo Texas | Construction of VFT Station allowing Asyncronous Connection for 100 MW transfer with CFE | 2005-11-20 | 2007-02-15 |  |  | 55000000 | [12 empty] | Pursuant to Subst. Rule 25.83(a)(3) |  | 55000000 | 0 | 55000000 |  |  | 55000000 | 0 | 0
4058727201 | City of Robstown to Robstown Tap Rebuild and Reconductor | Nueces, County Robstown, Texas | Rebuild and reconductor of 69 kV line from City of Robstown Utility Sub to Lon Hill to Robstown Subtation Tap (capable of 138 kV operation) | 2005-11-24 | 2007-01-08 | 2006-12-26 |  | 956563 |  |  | 100 | 69 |  | 0.82 | 795 ACSR | Single Pole Concrete or Steel | Centerline | 0.82 |  |  | Subst. Rule 25.101(c)(5)(B) |  | 956563 | 0 | 956563 |  |  | 956563 | 0 | 0
4061647901 | Naval Base to N. Padre Tap OPGW Installation | Nueces, County | Addition of OPGW to the Naval Base to N. Padre Tap Transmission line | 2006-10-23 | 2006-12-08 |  |  | 1053781 |  |  | 100 | [9 empty] | Pursuant to Subst. Rule 25.83(a)(3) |  | 1053781 | 0 | 1053781 |  |  | 1053781 | 0 | 0
40737194 | Laredo Plant to Anna Street 69 kV to 138 kV Conversion | Webb County, Texas | Conversion of the existing 69 kV transmission line circuit to 138 kV operation requiring change out of insulators and installation of some structures. | 2007-01-22 | 2007-02-07 |  |  | 686500 |  |  |  | 69 | 138 | 3.1 | (1) 795,000 cm AAC 19 Comp | Double ckt. steel and wood single pole | Centerline Defined | 3.1 |  |  | Sub.Rule 25.101(c)(5)(B) | Double Circuit Line with one side remaining 69kV and the other side converted to 138kV | 686500 | 0 | 686500 |  |  | 686500 | 0 | 0
40737194a | Laredo Plant to Anna Street OPGW Installation | Webb County, Texas | Addition of OPGW to the Laredo Plant to Anna Street Transmission line | 2007-01-22 | 2007-02-07 |  |  | 325565 | [12 empty] | Pursuant to Subst. Rule 25.83(a)(3) |  | 325565 | 0 | 325565 |  |  | 200000 | 125565 | 125565
40780619 | MidValley 69kV to 138kV Conversion | Hidalgo County, Texas | Loop S. McAllen to Weslaco 138 kV line into new Stewart Road Substation with 795 ACSS and OPGW wire | 2007-04-19 | 2007-12-07 | 2007-12-04 |  | 650000 |  |  | 95 | 138 | 138 | 0.8 | 795 kcmil ACSS 26/7 | Concrete or steel single pole | - | - | 100 | 0.4 | Sub.Rule 25.101(c)(5)(A) | Consent and easements obtained from landowner | 650000 | 0 | 650000 |  |  | 650000 | 0 | 125565
40780707 | MidValley 69kV to 138kV Conversion | Hidalgo County, Texas | Convert Stewart Rd Tap to MVEC Hi-Line with 795 ACSS and OPGW from 69 kV to 138 kV | 2007-08-01 | 2007-12-31 | 2007-11-19 |  | 1886980 |  |  | 95 | 69 | 138 | 3.2 | 795 kcmil ACSS 26/7 | Concrete or steel single pole | Centerline Defined |  |  |  | Sub.Rule 25.101(c)(5)(B) | The line is located in TCC single certified and in TCC / MVEC (Magic Valley) dual certified areas | 1886980 | 0 | 1886980 |  |  | 1886980 | 0 | 125565
40780682 | MidValley 69kV to 138kV Conversion | Hidalgo County, Texas | Convert MVEC Hi-Line to Hidalgo with 795 ACSS and OPGW from 69 kV to 138 kV | 2007-11-01 | 2008-02-28 | 2008-01-25 |  | 1741830 |  |  | 20 | 69 | 138 | 2.9 | 795 kcmil ACSS 26/7 | Concrete or steel single pole | Centerline Defined |  |  |  | Sub.Rule 25.101(c)(5)(B) | The line is located in TCC single certified and in TCC / MVEC (Magic Valley) dual certified areas | 1741830 | 0 | 1741830 |  |  | 1741830 | 0 | 125565
40780719 | MidValley 69kV to 138kV Conversion | Hidalgo County, Texas | Convert South McAllen to Hidalgo 69 kV to 138 kV with 795 and 1590 ACSS - with OPGW | 2008-01-01 | 2008-05-31 |  |  | 2623212 |  |  | 5 | 69 | 138 | 3.8 | 795 kcmil ACSS 26/7 | Concrete or steel single pole | Centerline Defined |  |  |  | Sub.Rule 25.101(c)(5)(B) | The line is located in TCC single certified and in TCC / MVEC (Magic Valley) dual certified areas | 2623212 | 0 | 2623212 |  |  | 2623212 | 0 | 125565
40449031 | Tap from N. Edinburg-Palmview 138kV Line to Palmhurst Sub | Hidalgo County | Rebuild approximately 1.7 miles of existing 69kV Bates to Palmhurst transmission line and convert to 138kV and tap into existing Edinburg to Palmview 138 kV line. Retire remaining 69 kV line to Bates. | 2007-04-24 | 2007-05-23 | 2007-06-09 |  | 1390000 |  |  | 95 | 69 | 138 | 1.7 | 1272 MCM ACSR | Steel Single Poles | Ceterline Defined | 1.7 |  |  | Sub. Rule 25.101(c) 5 (B) and 25.101(c) 5 (E) | The line is located in AEP TCC single and MVEC (Magic Valley) single certified areas. Some line movement to address encroachments (consent obtained) | 1390000 | 0 | 1390000 |  |  | 1390000 | 0 | 125565
40212890 | Flato Property / Mustang Island 69 kV Line Rebuild | Nueces County, City of Corpus Christi and Port Aransas, Texas | Rebuild and partially relocate 69 kV Line. Reconductor from 4/0 to 795 MCM ACSS. | 2007-05-14 | 2007-06-15 |  |  | 3266153 |  |  | 100 | 69 | 69 | 3.33 | 795 MCM ACSS | Steel Monopile w/ Concrete Pole | 60 | 3.33 | 60 | 2.1 | Pursuant to Subst. Rule 25.101 (c)(5) (B) | Portions of line will be relocated adjacent to SH 381 with landowner consent. | 3266153 | 0 | 3266153 |  |  | 3266153 | 0 | 125565
40212890a | Mustang Island/N. Padre Tap 69 kV Line Rebuild | Nueces County, City of Corpus Christi | Rebuild and relocate 69 kV Line. Reconductor from 4/0 to 795 MCM ACSS. | 2007-06-11 | 2007-07-15 |  |  | 3260671 |  |  | 95 | 69 | 69 | 3.42 | 795 MCM ACSS | Steel Monopile w/ Concrete Pole | 60 | 3.42 | 60 | 3.42 | Pursuant to Subst. Rule 25.101 (c)(5) (B) | Landowner Consent Obtained | 3260671 | 0 | 3260671 |  |  | 3260671 | 0 | 125565
40638212 | El Gato to Goolie 138 kV | Hidalgo County | Construct approximatly 5 miles of 138 kV line on pre-stressed concrete or steel structures, with a portion of the line double circuit capable. | 2008-10-13 | 2009-05-08 |  | 5346624 |  |  |  | 0 |  | 138 | 5 | 795 MCM ACSS | Pre-stressed concrete or steel single pole |  |  | 100 | 5 | 34050 | CCN filed on June 25, 2007. | 5346624 | 0 | 5346624 |  |  | 5346624 | 0 | 125565
40903730 | Kenedy Ranch 345 kV | Kenedy County | Construct approximatly 22 miles of 345 kV line on single pole steel structures, double circuit capable. | 2007-11-19 | 2008-09-01 |  | 35561645 |  |  |  | 0 |  | 345 | 22 | 2-1590 kcmil ACSR | Steel single pole |  |  | 150 | 22 | 34298 | CCN filed on June 25, 2007. | 35561645 | 0 | 35561645 |  |  | 35561645 | 0 | 125565
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
|  | 120039000 | 72023400 | Staff note: $72,023,400 is AEPC portion of AEPC/STEC project.
|  | Total | AEPC 60%
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 288628973 | 288628973
[24 empty] | 0 | 39 | 39 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H24: Allen Steven Boling: T-Line: $102,236,000; Station: $17,713,000. TOTAL: $121,749,000. AEPN - 60% ($72,023,000) STEC - 40% ($48,015,600)
Note on H39: Allen Steven Boling: Line: 5,346,624 Station: 2,594,468
Note on H40: Allen Steven Boling: Line: 35,561,645 Station: 2,594,469
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## AEPN
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
40424168 & 40474050 | Santa Anna-Bangs | Coleman County | Rebuild existing 69kV single wood pole line with double circuit 138/69 kV single steel pole construction, 795 ACSR conductor | 2005-01-24 | 2005-06-07 | 2005-06-07 |  | 5148800 | 4824012 | -6.308% | 100 | 69 | 69 and138 | 7.21 | 795 ACSR | Single Pole Steel, double circuit | center line | 7.21 | center line | 7.21 | Pursuant to Subst. Rules 25.101(c)(5)(B) and 25.101(c)(5)(C) | 100% consent obtained | 5148800 | 5148800 | 0 |  |  | 5148800 | 0 | 0
40817612 | TUEC SYNTX-37th St. Line Replacement of 3 structures for TxDOT | Snyder, Texas / Scurry County | Replacing 3 single pole concrete davit arm structures with taller structures of same type | 2007-01-08 | 2007-01-12 |  |  | 101000 |  |  |  | 69 |  |  |  | Concrete Pole | Undefined Hwy Right of Way |  |  |  | Subst. Rule 25.101 (c)(5)(F) | Structures Located in TxDOT Right of Way | 101000 | 0 | 101000
40769903 | Rebuild Elmdale - Clyde 69-kV line | Taylor, Callahan Co. (City of Clyde) | Rebuild and Reconductor the 69-kV line from Elmdale to Clyde (138-kV double ckt. capable) | 2007-04-27 | 2007-08-31 |  |  | 8468192 |  |  |  | 69 | 69 | 8.5 | 795 ACSR | Single pole steel | centerline | 8.5 | 100 | 7.4 | Sub. Rule 25.101(c)(5)(B) | Consent obtained from majority of landowners to supplement existing easement. Where consent not obtained the structure will not be upgradable to 138 kV. | 8468192 | 0 | 8468192 |  |  | 8468192 | 0 | 0
40839051 | Whirlwind Generation Interconnect | Motley County, City of Matador | Modify Matador Substation to accept new 69 kV line from wind farm. Substation equipement upgrades at other local substations for increase power transfer requirement. | 2007-05-03 | 2007-09-24 | 2007-09-25 |  | 3597100 |  |  | 99 | 69 | 69 | [7 empty] | Pursuant to Sub. Rule 25.83 (a)(3) |  | 3597100 | 0 | 3597100 |  |  | 3597100 | 0 | 0
40833618 | Yellow Jacket Sub | Menard Co. | Construct new transmission substation - Add two 90 MVA autos 69/138kV LTC with cap banks & SCADA. | 2007-04-03 | 2008-05-01 | 2007-11-07 |  | 7945000 |  |  | 70% | 138 | 138 | [7 empty] | Pursuant to Sub. Rule 25.83 (a)(3) |  | 7945000 | 0 | 7945000 |  |  | 7945000 | 0 | 0
40872056 | N. Angelo to College Hills 138kV Cut-in | Tom Green County, City of San Angelo | Modify 138kV line to enter and exit new Bluffs distribuition substation | 2007-07-31 | 2007-11-01 | 2007-12-10 |  | 412236 |  |  | 99% | 138 | 138 |  | 795 Drake | Single pole steel | on utility propery | .1 mi. | center line | 0.15 | Subst. Rule 25.101(c)(5)(A) | TNC owns property. | 412236 | 0 | 412236 |  |  | 412236 | 0 | 0
40906389 | S. Abilene to Putnam 138kV line capacity upgrade | Taylor, Callahan Counties | Replace approximately 35% of existing wood H-frame structures with taller H-frame steel structures and add some additional dead ends | 2007-10-01 | 2008-09-01 |  |  | 4096800 |  |  |  | 138 |  | 36.4 | 4/0 ACSR | Steel H-Frame | Centerline defined | 36.4 |  |  | Subst. Rule 25.101 (c)(5) (B) | No new ROW required. Increases loading capacity and improves reliablity. | 4096800 | 0 | 4096800 |  |  | 4096800 | 0 | 0
40917769 | Eden-Menard Hwy 83 Line Relocation for TXDOT | Concho County | Reroute for Highway 83 expansion, providing two new perpendicular crossings | 2007-09-13 | 2007-11-10 |  |  | 1576000 |  |  |  | 69 |  | 0.6 | 336 ACSR | Steel Single Pole |  |  | 60 | 0.6 | Subst. Rule 25.101 (c)(5) (F) | Consent obtained and responsive to TXDOT request. | 1576000 | 0 | 1576000 |  |  | 1576000 | 0 | 0
40772038 | Rebuild and Reconductor Clyde to Putnam 69kV line | Callahan | Rebuild and Reconductor of 69kV line from Clyde to Putnam (capable of double circuit 138kV operation) | 2007-11-12 | 2008-04-11 |  |  | 21218766 |  |  |  | 69kV |  | 19.6 | 795 ACSR | Single pole steel | centerline | 3.08 | 100 | 16.52 | Sub. Rule 25.101(c)(5)(B) | Consent obtained from majority of landowners to supplement existing easement. Where consent not obtained the structure will not be upgradable to 138 kV. | 21218766 | 0 | 21218766 |  |  | 21218766 | 0 | 0
40765392 | Rebuild and Reconductor Elm Creek to Shelton St. 69kV line | Taylor | Rebuild and Reconductor of 69kV line from Abilene Elm Creek to Shelton St(capable of single ckt 138 kV operation) | 2007-10-15 | 2007-12-31 |  |  | 5152300 |  |  |  | 69kV |  | 2.62 | 795 ACSR | Single pole steel | centerline | 2.62 | n/a | 2.62 | Sub. Rule 25.101(c)(5)(B) | City of Abilene ROW. City Noticed. | 5152300 | 0 | 5152300 |  |  | 5152300 | 0 | 0
40769903 | Rebuild and Reconductor Abilene Plant to Elmdale 69kV line | Taylor, Callahan | Rebuild and Reconductor of 69kV line from Abilene Plant to Elmdale (Capable of double circuit 138kV) | 2007-10-15 | 2008-02-01 |  |  | 2589000 |  |  |  | 69kV |  | 4.9 | 795 ACSR | Single pole steel | centerline | 2.59 | 100 | 2.31 | Sub. Rule 25.101(c)(5)(B) | Majority of rebuild/reconductor is in existing City of Abilene ROW and where consent from landowners to supplement easement has been obtained.Where consent not obtained the structure will not be upgradable to 138 kV. | 2589000 | 0 | 2589000 |  |  | 8468192 | -5879192 | -5879192
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 4824012 | 5148800 | 55156394 | 60305194
[24 empty] | 1 | 10 | 11 | Project Count
[24 empty] | Completed | Active | Total
Note on A23: Allen Steven Boling: STAFF MODIFIED PROJECT NUMBER TO ALLOW ERROR CHECKING. (DUPLICATE PROJECT NUMBER)
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AD3: Allen Steven Boling: FORMULA DELETED TO ALLOW CHECKING PROJECT INCLUDED IN MUNDAY-THROCKMORTON PROJECT NO 40385791
Note on AE3: Allen Steven Boling: FORMULA DELETED TO ALLOW CHECKING PROJECT INCLUDED IN MUNDAY-THROCKMORTON PROJECT NO 40385791
Note on AF3: Allen Steven Boling: FORMULA DELETED TO ALLOW CHECKING PROJECT INCLUDED IN MUNDAY-THROCKMORTON PROJECT NO 40385791

## BEPC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
04009 | Booneville to Hearne | Robertson & Brazos County | Rebuilding of approx. 23 miles of 138 kV 795 MCM line from existing Booneville sub. to existing Hearne sub. | 2003-06-01 | 2003-08-15 |  | 7989950 |  |  |  | 30% | 138 |  | 23 | 795 MCM | Single Pole Concrete | 60 | 23 |  |  | 25.101(c)(2)(C)(ii) | Affidavit attached with filing (April 2007). | 7989950 | 0 | 7989950 |  |  | 7989950 | 0 | 0
02012 | Fairview - Aledo | Hood & Parker County | Construct approximately 26 miles of new single-pole 138 kV 795 MCM transmission line from the existing radial fed BEPC Fairview substation to the existing radial fed BEPC Aledo substation. In addition, this project will include rebuilding approximately 5.8 miles of existing transmission line from the BEPC Waples substation to the BEPC Fairview substation. Also, included in the project is the construction of a switching station at Dicey and the addition of a 138 kV breaker at Waples substation. | 2008-06-06 | 2009-03-08 |  | 13340000 |  |  |  | 0% | NA | 138 | 26 | 795 MCM | Single Pole Concrete or Steel | NA | NA | 70 | 26 | 28254 | CCN Application Filed on August 15, 2003 | 13340000 | 0 | 13340000 |  |  | 13340000 | 0 | 0
0207420 | Jessica Loop | Johnson | Construct 3 miles of double circuit line from tap to Jessica Sub. | 2006-11-01 | 2007-05-05 | 2007-06-15 | 2413000 | 2012471 |  |  | 100% | 138 | 138 | 2.75 mi. | 795 ACSR | Single Pole Concrete or Steel | NA | 2.75 mi. | 70 | 2.75 mi. | Docket No. 30365 | CCN Filed Nov. 8, 2004 | 2012471 | 0 | 2012471 |  |  | 2012471 | 0 | 0
0302021 | Whitney to Covington | Bosque, Hill & Johnson | Rebuild 27.85 miles of line from Whitney to Covington with 1033 ASCR | 2006-02-01 | 2006-06-01 |  | 5000000 | 8266724 |  |  | 100% | 138 | 138 | 27.85 mi | 1033 ACSR | Single Pole Concrete or Steel | 100 | 27.85 mi | 100 | 27.85 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 8266724 | 0 | 8266724 |  |  | 8266724 | 0 | 0
0301921 | Poage to Santa Fe | Bosque, Hill & Johnson | Rebuild 24.01 miles of line from Poage to Leon Junction with 795 ASCR | 2006-03-01 | 2006-07-01 |  | 4250000 | 7029463 |  |  | 100% | 69 | 138 | 24.01 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 24.01 mi | 70 | 24.01 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 7029463 | 0 | 7029463 |  |  | 7029463 | 0 | 0
0302521 | Prairie Hill to Purdon | Limestone , Navarro | Rebuild 24.28 miles of line from Prairie Hill to Purdon with 795 ASCR | 2006-10-01 | 2006-01-01 |  | 7250000 | 6300000 |  |  | 100% | 138 | 138 | 24.28 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 24.28 mi | 60 | 24.28 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 6300000 | 0 | 6300000 |  |  | 6300000 | 0 | 0
0203022 | Peoria - Forreston | Ellis, Hill | Rebuild 30.94 miles of line from Peoria to Itasca with 795 ASCR | 2006-05-01 | 2006-10-01 |  | 9250000 | 8080566 |  |  | 100% | 138 | 138 | 30.94 mi | 795 ACSR | Single Pole Concrete or Steel | 100 | 30.94 mi | 100 | 30.94 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 8080566 | 0 | 8080566 |  |  | 8080566 | 0 | 0
0401320 | Frisco - Krugerville Rebuild | Denton | Rebuild 8.0 miles of line from Frisco to Krugerville with 1590 ASCR | 2006-11-15 | 2007-02-15 |  | 3560000 |  |  |  | 0% | 138 | 138 | 8.0 mi. | 1590 ACSR | Single Pole Concrete or Steel | 100 | 8.0 mi. | 100 | 8.0 mi. | 25.101(c)(5)(B) | Affidavit at a later date closer to scheduled construction start | 3560000 | 0 | 3560000 |  |  | 3560000 | 0 | 0
4076 | Branchville - Silver City | Milam, Robertson | Rebuild 9.90 miles of line from Branchville to Silver City with 795 ASCR | 2006-12-01 | 2007-05-15 |  | 3712500 | 3155950 |  |  | 100% | 138 | 138 | 9.9 | 795 ACSR | Single Pole Concrete or Steel | 60 | 9.9 | 60 | 9.9 | 25.101(c)(5)(B) | Affidavit attached with filing. (6/1/06) | 3155950 | 0 | 3155950 |  |  | 3155950 | 0 | 0
303020 | Hood - De Cordova - Spunky | Hood, Somerville, Johnson | Rebuild 11.69 miles of line from Hood to Spunky with 795 ASCR | 2007-04-01 | 2007-07-01 |  | 4383750 | 4917400 |  |  | 95% | 138 | 138 | 11.69 | 795 ACSR | Single Pole Concrete or Steel | 60 | 11.69 | 60 | 11.69 | 25.101(c)(5)(B) | Affidavit attached with filing. | 4917400 | 0 | 4917400 |  |  | 4917400 | 0 | 0
302620 | Hilltop Lakes - Petteway | Robertson & Leon | Construct 8.28 miles of single circuit line from Hilltop Lake to Petteway | 2007-02-08 | 2007-06-08 |  | 2732400 |  |  |  | 100% | 69 | 138 | 8.28 mi. | 795 ACSR | Single Pole Concrete or Steel | 60 | 8.28 mi. | 60 | 8.28 mi. | 25.101(c)(5)(B) | Affidavit attached with filing. | 2732400 | 0 | 2732400 |  |  | 2732400 | 0 | 0
600820 | Granbury - Stephenville | Erath, Hood | Rebuild 26.16 miles of line from Granbury to Stephenvillewith 795 ASCR | 2007-02-15 | 2007-08-10 |  | 8632800 | 8000000 |  |  | 100% | 69 | 138 | 26.16 mi | 795 ACSR | Single Pole Concrete or Steel | 60 | 26.16 mi | 60 | 26.16 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 8000000 | 0 | 8000000 |  |  | 8000000 | 0 | 0
607210 | Wildcat | Johnson, Hood | Construct 8.5 miles of new 138 kV single circuit transmission from Wildcat Tap to Wildcat Sub | 2008-07-07 | 2009-01-01 |  | 3655000 |  |  |  | 0% | 138 | 138 | 8.5 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 8.5 mi. | 70 | 8.5 mi. | 33800 | CCN Filed 01/30/07 | 3655000 | 0 | 3655000 |  |  | 3655000 | 0 | 0
303611 | Mustang Loop | Denton | Construct 8.0 miles of new 138 kV double circuit transmission from Mustang Tap to Mustang Sub | 2007-11-07 | 2008-01-01 |  | 4019031 |  |  |  | 0% | 138 | 138 | 17.0 mi | 1590 ACSR | Single Pole Concrete or Steel | NA | 8.0 mi. | 70 | 8.0 mi. | 32871 | CCN Filed 07/06/06 | 4019031 | 0 | 4019031 |  |  | 4019031 | 0 | 0
302722 | Olney - Shannon | Archer, Clay & Young | Rebuild 28.53 miles of line from Olney to Shannon with 1033 ACSR | 2008-02-08 | 2008-06-06 |  | 10841400 |  |  |  | 35% | 69 | 138 | 28.63 mi | 1033 ACSR | Single Pole Concrete or Steel | NA | 28.63 mi | 70 | 28.63 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 10841400 | 0 | 10841400 |  |  | 10841400 | 0 | 0
407420 | Pancake - Gatesville | Coryell | Rebuild 3.98 miles of line from Pancake to Gatesville with 795 ACSR | 2007-10-15 | 2008-02-15 |  | 1592000 | 800000 |  |  | 100% | 69 | 138 | 3.98 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 3.98 mi | 60 | 3.98 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 800000 | 0 | 800000 |  |  | 800000 | 0 | 0
500820 | Gatesville - Santa Fe Sw. | Coryell | Rebuild 11.43 miles of line from Gatesville to Santa Fe Switch with 795 ACSR | 2007-10-15 | 2008-02-15 |  | 4572000 |  |  |  | 55% | 69 | 138 | 11.43 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 11.43 mi | 60 | 11.43 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 4572000 | 0 | 4572000 |  |  | 4572000 | 0 | 0
400720 | Hasse - Downing | Comanche | Rebuild 7.34 miles of line from Hasse - Downing with 795 ACSR | 2007-11-15 | 2008-03-15 |  | 2936000 |  |  |  | 20% | 69 | 138 | 7.34 mi | 795 ACSR | Single Pole Concrete or Steel | NA | 7.34 mi | 60 | 7.34 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 2936000 | 0 | 2936000 |  |  | 2936000 | 0 | 0
407310 | Bell County - Schwertner | Bell ,Williamson | Rebuild 13.69 miles of line from Bell County Sw. to Schwertner Sub. | 2007-11-01 | 2008-02-15 |  | 5476000 |  |  |  | 0% | 69 | 138 | 13.69 mi | 959 ACSS - TW | Single Pole Concrete or Steel | NA | 13.69 mi | 60 | 13.69 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 5476000 | 0 | 5476000 |  |  | 5476000 | 0 | 0
406410 | Gabriel - Schwertner | Williamson | Rebuild 12.94 miles of line from Gabriel Sw. to Schwertner Sub. | 2007-11-10 | 2008-03-15 |  | 5176000 |  |  |  | 15% | 69 | 138 | 12.94 mi | 959 ACSS - TW | Single Pole Concrete or Steel | NA | 12.94 mi | 60 | 12.94 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 5176000 | 0 | 5176000 |  |  | 5176000 | 0 | 0
501220 | Bunker - Hood | Hood | Rebuild 9.05 miles of line from Bunker Sub to Hood Sub. | 2007-11-10 | 2008-03-15 |  | 3975000 |  |  |  | 20% | 69 | 138 | 9.05 mi | 1590 ACSR | Single Pole Concrete or Steel | NA | 9.05 mi | 60 | 9.05 mi | 25.101(c)(5)(B) | Affidavit attached with filing. | 3975000 | 0 | 3975000 |  |  | 3975000 | 0 | 0
500412 | Craig Ranch | Collin | Construct 2.0 miles of line from tap to Craig Ranch Sub. | 2009-01-02 | 2009-05-02 |  | 9000000 |  |  |  | 0% | NA | 138 | 4.0 mi. | 1590 ACSR | Single Pole Concrete or Steel | NA | NA | 70 | 2.0 mi. | 34276 | CCN Filed 05/15/07 | 9000000 | 0 | 9000000 |  |  | 9000000 | 0 | 0
06006 | Hilltop Lakes Sw. - Hearne | Robertson | Rebuild 14.49 miles of line from Hilltop Lakes Sw to Hearne Sub. | 2008-05-04 | 2008-09-04 |  | 6013350 |  |  |  | 0% | 69 | 138 | 14.49 mi. | 795 ACSR | Single Pole Concrete or Steel | 60 | 14.49 mi. | 60 | 14.49 mi. | 25.101(c)(5)(B) | Affidavit to be filed at a later date | 6013350 | 0 | 6013350 |  |  | 6013350 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
NOTE: PROJECT NO 01006 (NORTH TEXAS - COTTONDALE) WAS ORIGINALLY LEFT IN THIS MONTH AFTER BEING CLOSED LAST MONTH.
| PUCT STAFF REMOVED THE PROJECT. | [21 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 131848705 | 131848705
[24 empty] | 0 | 23 | 23 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H3: Allen Steven Boling: Line: $ 13.340 ; Station: $ 3.034 ; Total: $ 16.374
Note on H4: Allen Steven Boling: Line: $2.400; Station: $2.100; Total: $4.500
Note on H14: Allen Steven Boling: Line: $3.655; Station: $2.597; Total: $6.252
Note on H15: Allen Steven Boling: Revised Application: Line: $4.0190; Station: $2.742; Total: $6.671 Original: Line: $8.305; Station: $2.742; Total: $11.047
Note on H23: Allen Steven Boling: Line: $ 9.000 ; Station: $ 3.053 ; Total: $ 12.053
Note on I1: aboling: Please enter only a single integer, if possible.
Note on I4: Allen Steven Boling: Line: $2.015; Station: $1.026; Total: $3.039
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AD2: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD27: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD29: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD30: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE2: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE27: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE29: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE30: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF2: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF27: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF29: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF30: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.

## CNP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
547 | Freeport LNG (QNTANA) | Freeport, Quintana, Brazoria | 69 kV Service to Customer-owned QNTANA Substation from Ckt. 47B | 2006-10-23 | 2007-11-01 | 2007-08-03 | 6395000 | 11200000 | 10183215.57 | -9.078% | 100% | 69 | NA | 7.8 | 1433.6 ACSS | Concrete Poles, Steel Poles, Steel Towers | NA | NA | 50-100 | 3.9 | Docket No. 30617 | Construction Complete. Final Order signed 3/22/06. Actual cost of Transmission Facilities and Substation Relay and SCADA equipment to be reimbursed by Freeport LNG. Last time to report. See Docket No. 30617 tab for variance explanation. | 11200000 | 11200000 | 0 |  |  | 11200000 | 0 | 0
573 | 345 kV Hillje Project | Thompsons, Fort Bend, Wharton, Matagorda and Brazoria Counties | Construct a new double-circuit 345 kV transmission line and install an additional 345 kV circuit on an existing transmission line | 2006-03-13 | 2007-12-15 | 2007-07-31 | 80050000 | 80050000 |  |  | 99% | NA | 345 | 117.2 | 2-1433.6 ACSS, 2-795 ACSR | Steel Towers | 200-400 | 46.3 | 90-125 | 22 | Docket No. 31591 | Construction Complete. Final Order signed 2/13/06. | 80050000 | 0 | 80050000 | 285000 |  | 80050000 | 0 | 0
2006.1 | LaMarque - Webster | Webster, Harris, League City, Dickinson, Texas City, LaMarque, Galveston | Routine maintenance of 69 kV Ckt. 13B | 2006-11-06 | 2008-04-15 |  | 350000 | 366000 |  |  | 85% | 69 | NA | 15.9 | 397 ACSR, 927 ACAR, 795 AAC | Wood Poles, Steel Towers, Steel Poles | 70-1220 | 15.9 | NA | NA | 25.83 (a)(3) |  | 366000 | 0 | 366000 | 14765000 |  | 366000 | 0 | 0
677 | Wharton - CANEY_ Corner | Wharton, Wharton | Reconductor and Rebuild of 138 kV Ckt. 60B; 138kV Service to CANEY_ Substation within one mile of Ckt. 60B | 2007-05-09 | 2008-01-31 |  | 569000 | 709000 |  |  | 99% | 138 | NA | 1 | 2-959.6 ACSS | Concrete Poles, Steel Towers | 80 | 0.5 | NA | NA | 25.101(c)(5)(B); 25.101(c)(5)(A) | Construction Complete. | 709000 | 0 | 709000 |  |  | 709000 | 0 | 0
677.1 | CANEY_ Corner - East Bernard | Wharton, East Bernard, Wharton | Reconductor and Rebuild of 138 kV Ckt. 60B | 2007-05-07 | 2008-03-01 |  | 6163000 | 8463000 |  |  | 95% | 138 | NA | 14.4 | 2-959.6 ACSS | Concrete Poles, Steel Towers | 80 | 14.4 | NA | NA | 25.101(c)(5)(B) |  | 8463000 | 0 | 8463000 |  |  | 8463000 | 0 | 0
2006.2 | Angleton - PETSON | Danbury, Alvin, Brazoria | Routine maintenance of 138 kV Ckt. 04C | 2008-04-21 | 2008-06-06 |  | 344000 | 414000 |  |  | 0% | 138 | NA | 15.7 | 795 ACSR, 795 AAC | Steel Towers, Wooden H-Frames, Wood Poles, Steel Poles | 60-145 | 15.7 | NA | NA | 25.83 (a)(3) |  | 414000 | 0 | 414000 |  |  | 414000 | 0 | 0
515 | U.S. Highway 90E | Houston, Harris | Alteration of 69 kV Ckts. 17A, 20C, 38A, 38B; 138kV Ckts. 03F, 08E, 08F, 70D, 77A; and 345kV Ckts. 74F and 75C as requested by TxDOT for highway construction | 2007-08-20 | 2008-02-05 |  | 2161000 | 3191000 |  |  | 99% | 69, 138, 345 | NA | 2.8 | 795 AAC, 2-795 ACSR, 2-959.6 ACSS, 2-795 AAC, 2-2167 ACSR | Steel Towers, Steel Poles, Concrete Poles | 20-200, Street | 1 | NA | NA | 25.101(c)(5)(F) | Construction Complete. Actual cost to be reimbursed by TxDOT. | 3191000 | 0 | 3191000 |  |  | 3191000 | 0 | 0
677.2 | East Bernard - Fort Bend | East Bernard, Wharton, Rosenberg, Fort Bend | Reconductor and Rebuild of 138 kV Ckt. 60A | 2007-12-10 | 2008-06-20 |  |  | 7305000 |  |  | 25% | 138 |  | 18.8 | 2-959.6 ACSS | Steel Towers, Steel Poles, Concrete Poles | 10-355 | 18.8 |  |  | 25.101(c)(5)(B) |  | 7305000 | 0 | 7305000 |  |  | 7305000 | 0 | 0
619 | University of Texas M.D. Anderson Cancer Center | Houston, Harris | Relocation of a portion of 138 kV Ckt. 08I at the request of and the expense of M.D. Anderson Cancer Center on right-of-way provided by the Board of Regents, University of Texas System on behalf of the University of Texas M.D. Anderson Cancer Center. | 2008-04-01 | 2008-08-11 |  |  | 4000000 |  |  | 0% | 138 |  | 0.4 | 4000 CU | Steel Poles, Underground Cable | Street | 0.19 | 30-138 | 0.4 | 25.101(c)(5)(D) | Actual cost to be reimbursed by The University of Texas M.D. Anderson Cancer Center. | 4000000 | 0 | 4000000 |  |  | 4000000 | 0 | 0
692 | Singleton Substation | Grimes | 345 kV service to Singleton Substation within one mile of Ckts. 74C, 75D, 98D and 99D | 2008-02-11 | 2009-03-01 |  |  | 4492000 |  |  | 5% | 345 |  | 1.2 | 2-795 ACSR, 2-1590 ACSR | Steel Towers | Substation Property | 0.6 |  |  | 25.101(c)(5)(A) |  | 4492000 | 0 | 4492000 |  |  | 3340000 | 1152000 | 1152000
692.1 | CNP-TMPA Singleton Interconnection | Grimes | Reconfiguration of 345 kV TMPA Ckts. 75D & 99D for Singleton Substation Construction | 2008-02-11 | 2009-03-01 |  |  | 2368000 |  |  | 5% | 345 |  | 0.3 | 2-1590 ACSR | Steel Towers | Substation Property, 150 | 0.15 |  |  | 25.83 (a)(3) |  | 2368000 | 0 | 2368000 |  |  | 2160000 | 208000 | 1360000
662 | S.R. Bertron-Fairmont | La Porte, Deer Park, Harris | Partial Rebuild and Partial Reconductor of 138 kV Ckts. 06A & 06B, Installation of an additional 138kV circuit on existing double-circuit structures | 2008-03-15 | 2008-05-15 |  |  | 1400000 |  |  | 0% | 138 |  | 7.7 | 2-795 AAC, 2-959.6 ACSS | Steel Towers, Concrete Poles, Wood H-Frames | 150-710 | 7.7 |  |  | 25.101(c)(5)(B); 25.83 (a)(3) |  | 1400000 | 0 | 1400000 |  |  | 1400000 | 0 | 1360000
9 | Jackson Hill Street | Houston, Harris | Partial alteration of 69 kV Ckt. 31C to eliminate existing encroachments of residential buildings | 2008-06-01 | 2008-10-01 |  |  | 306000 |  |  | 0% | 69 |  | 0.5 | 795 AAC | Steel Poles | Street | 0.5 |  |  | 25.101(c)(5)(E) |  | 306000 | 0 | 306000 |  |  | 306000 | 0 | 1360000
691 | BENDER Substation | Chambers | 138 kV service to BENDER Substation within one mile of Ckt. 86D | 2008-04-30 | 2008-06-01 |  |  | 224000 |  |  | 0% | 138 |  | 0.2 | 2-795 ACSR | Steel Towers, Concrete Poles | 350 | 0.06 | 200 | 0.04 | 25.101(c)(5)(A) | Actual cost to be reimbursed by LDH Energy Mont Belvieu, L.P. | 224000 | 0 | 224000 |  |  | 216000 | 8000 | 1368000
599 | I-45 @ SH 96 | League City, Galveston | Alteration of 345 kV Ckt. 99A and 138 kV Ckt. 93B as requested by TxDOT for highway construction | 2008-08-01 | 2008-09-01 |  |  | 280000 |  |  | 0% | 138, 345 |  | 1 | 2-795 ACSR, 2-927 ACAR | Steel Towers | 225 | 0.5 |  |  | 25.101(c)(5)(F) | Actual cost to be reimbursed by TxDOT. | 280000 | 0 | 280000 |  |  | 280000 | 0 | 1368000
2008 | W.A. Parish-Britmoore | Thompsons, Sugar Land, Stafford, Fort Bend Houston, Harris | Routine maintenance of 138 kV Ckt. 09A | 2008-04-01 | 2008-06-01 |  |  | 398000 |  |  | 0% | 138 |  | 23.64 | 2-795 AAC, 2-795 ACSR, 2000 AAC | Wood H-Frames, Steel Towers, Steel Poles, Concrete Poles | 150-745 | 23.6 |  |  | 25.83 (a)(3) |  | 398000 | 0 | 398000 |  |  | 253000 | 145000 | 1513000
671.1 | METRO North Main Street | Houston, Harris | Alteration of 138 kV Ckt. 21B as requested by METRO for railway and road construction | 2008-09-01 | 2008-10-01 |  |  | 167000 |  |  | 0% | 138 |  | 0.26 | 2000 AAC | Concrete Poles | 20-75, Street | 0.3 |  |  | 25.101(c)(5)(F) | Actual cost to be reimbursed by METRO. | 167000 | 0 | 167000 |  |  | 167000 | 0 | 1513000
671.2 | METRO North Corridor | Houston, Harris | Alteration of 138 kV Ckts. 03D and 21J as requested by METRO for railway construction | 2008-09-01 | 2008-10-15 |  |  | 253000 |  |  | 0% | 138 |  | 0.4 | 2-795 AAC | Steel Towers | 50 | 0.18 |  |  | 25.101(c)(5)(F) | Actual cost to be reimbursed by METRO. | 253000 | 0 | 253000 |  |  | 236000 | 17000 | 1530000
698 | Jefferson Corner-Pasadena | Pasadena, Harris | Reconductor & Partial Rebuild of 138 kV Ckt 06G | 2008-04-15 | 2008-06-30 |  |  | 1603000 |  |  | 0% | 138 |  | 4.6 | 2-959.6 ACSS | Steel Towers, Concrete Poles | 100-210 | 4.6 |  |  | 25.101(c)(5)(B) | New Project | 1603000 | 0 | 1603000 |  |  | #N/A | #N/A | #N/A
|  | 4 new projects | 2421000 | [20 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[24 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[24 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[24 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[24 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[24 empty] | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 10183215.57 | 11200000 | 115989000 | 127189000
[24 empty] | 1 | 18 | 19 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H2: Allen Steven Boling: $6,395,000 TRANSMISSION LINE AND $190,000 SUBSTATION.
Note on H3: Allen Steven Boling: $80,050,000 TRANSMISSION LINE AND $14,765,000 SUBSTATION.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on I2: Allen Steven Boling: FINAL ESTIMATED COST: $11,200,000 TRANS AND $285,000 SUBSTATION.
Note on I3: Allen Steven Boling: $80,050,000 TRANSMISSION LINE AND $14,765,000 SUBSTATION.
Note on J2: Allen Steven Boling: This line cost was originally $10,163,216 in this report, but cost analysis showed $10,183,216, so Staff changed this cost to the version in the cost analysis.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## DSEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
33755+ | Sub 22 transmission project | Castro, Parmer Counties | New 115 kv transmission line to existing Substation. Build new Station along Path and eventually convert existing station to 115 kv | 2006-03-15 |  |  | 3815000 | 3815000 |  |  | 60% | na | 115 | 18.3 | 397.5 kcmil 26/7 ACSR | wood poles, Concrete Poles | na | na | 20, 40 | 18.3 | 33000 |  | 3815000 | 0 | 3815000 | 1989000 |  | 3815000 | 0 | 0
33757 | Sub 23 | Deaf Smith County | Install new 12 mVa station along existing transmission line. | 2007-05-30 |  |  | na | 1280000 |  |  | 85% | 69 | na | na | na | na | na | na | na | na | 25.101(c)(2) |  | 1280000 | 0 | 1280000 |  |  | 1280000 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 5095000 | 5095000
[24 empty] | 0 | 2 | 2 | Project Count
[24 empty] | Completed | Active | Total
Note on H2: Allen Steven Boling: $3,815,000 T-Line $2,005,000 Substations
Note on I2: Allen Steven Boling: $3,815,000 T-Line $1,989,000 Substations

## EGSI
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
TL4433 | Johnstown-Porter Construct New 230kV Transmission Line | Montgomery County, TX | Construct 4.9 miles of single pole double circuit designed 230kV transmission line from Porter Substation to the new Johnstown Substation | 2009-05-15 | na | na | 5332055 |  |  |  |  | na | 230 | 9.8 | Bundled 954 ACSR | Concrete or Steel | na | na | 100 | 4.9 | 29420 | Revised Final Estimate not complete. Will report next month | 5332055 | 0 | 5332055 |  |  | 5332055 | 0 | 0
TL9965 | Port Acres Bulk to Keith Lake 230kV Transmission Line Project | Jefferson County, Texas | Construct new 230Kv double circuit transmission line fron the existing Port Acres Bulk Substation to the new Keith Lake Substation at the new Golden Pass LNG Facility | 2008-03-01 | na | na | 21690000 |  |  |  |  | na | 230 | 22.4 | 666 ACSR | Single Pole & H-Frame Double Circuit | na | na | 100 | 11.2 | 31198 | Design has begun. R/W acquisition is ongoing. | 21690000 | 0 | 21690000 |  |  | 21690000 | 0 | 0
TL5400 | Proposed Merlin Substation to L-17 138kV Transmission Line | Orange County, Texas | Construct new 138kV single pole double circuit transmission line from the new proposed Merlin Substation to the existing line 17 | 2009-03-01 | na | na | 3142673 |  |  |  |  | na | 138 | 2.6 | Bundled 666 ACSR | Single Pole Steel & Concrete | na | na | 100 | 2.6 | 31241 | This project was delayed as a result of Hurricane Rita. R/W acquisition is complete. | 3142673 | 0 | 3142673 |  |  | 3142673 | 0 | 0
TL4530 | Jayhawker-Security: Reroute L-811 at Security Landfill | Montgomery County, TX | Construct 1.4 MI single pole single circuit reroute of 138kV L-811 at Waste Management's Security Landfill | 2007-08-20 | 2007-10-25 | 2007-10-26 |  | 1550000 |  |  | 100 | 138 | na | 1.4 | 666 ACSR | Simgle Pole Steel & Concrete | 100 | 0.7 | 100 | 1.4 | 25.101(c)(5)(D)(i)(ii) | Working on final Costs. | 1550000 | 0 | 1550000 |  |  | 1550000 | 0 | 0
TL8571 | L-871 Relocate for TxDot Widening Project | Liberty County, TX | Relocate 3 Structures on 138kV Line 871 for TxDot Hwy Widening Project | 2008-02-29 |  |  | 283294 |  |  |  |  | 138 | na | na | 649 ACAR | Concrete | 100 | 0.02 | na | na | 25.101(c)(5)(F)(i)(ii) | Existing conductor will be relocated to new structures | 283294 | 0 | 283294 |  |  | 283294 | 0 | 0
TL 8550 | L-50 Relocate for TxDot Widening Project | Liberty county, TX | Relocate 2 structures on 138kV Line 50 for TxDot Hwy Widening Project | 2008-03-05 |  |  | 184378 |  |  |  |  | 138 | na | na | 4/0 ACSR | Concrete | 100 | 0.01 | na | na | 25.101(c)(5)(F)(i)(ii) | Existing conductor will be relocated to new structures | 184378 | 0 | 184378 |  |  | 184378 | 0 | 0
TL 8808 | L-808 Relocate for TxDot Widening Project | Liberty County, TX | Relocate 4 Structures on 138kV Line 808 for TxDot Hwy Widening Project | 2008-03-20 |  |  | 321038 |  |  |  |  | 138 | na | na | 649 ACAR | Concrete | 100 | 0.34 | na | na | 25.101(c)(5)(F)(i)(ii) | Existing conductor will be relocated to new structures | 321038 | 0 | 321038 |  |  | 321038 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 32503438 | 32503438
[24 empty] | 0 | 7 | 7 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H2: Allen Steven Boling: Line: 5,332,055 Station: $ 3,062,767 TOTAL: $8,384,822
Note on H3: Allen Steven Boling: Line: 21,690,000Station: $ 6,990,000 TOTAL: $28,680,000
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## EPE
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
TL145 | Montwood to Coyote 115kV Line (12600 Line) | El Paso, El Paso | As a part of the overall Eastside Expansion Plan, a new line is to be constructed between Montwood and Coyote Substations. The new line will be constructed utilizing single pole steel structures. The preferred route is approximately 7.8 miles in length. | 2008-04-21 |  |  | 1634174 | [5 empty] | 115 | 7.84 | 954 ACSR, single conductor, single circuit | 90' galvanized steel monopole structures. | Street ROW - franchise | 0.29 | 100, 15 overhang | 2.94, 4.61 | 24666 | Preparing construction bid packages. Anticipate construction to begin mid-April. | 1634174 | 0 | 1634174 | 568230 |  | 1634174 | 0 | 0
TL102 | Santa Teresa - Montoya 115 kV Line | El Paso, El Paso | Construct approximately 7.19 miles of 115kV transmission line on single pole structures to complete an electrical loop between Santa Teresa Substation (Dona Ana County, NM.) and Montoya Substation (El Paso County, TX). The project is intended to improve service reliability and provide for future electrical load growth in the project area. | 2008-08-01 |  |  | 5335988 | [5 empty] | 115 | 7.19 | 954 ACSR, single conductor, single circuit | 95' galvanized steel monopole structures. | Street ROW - franchise | 2.29 | 25, 50, 100 | 2.29, 4.76, 0.14 | 26670 | Row acquisition continues. | 5335988 | 0 | 5335988 |  |  | 5335988 | 0 | 0
TL117 | SFPP - Proposed 115 kV Transmission Line | El Paso, El Paso | Construct approximately 9.5 miles of 115 kV transmission circuit to provide transmission service to a petroleum storage and pumping facility. The project will involve adding a second circuit to an existing line previously constructed for double circuit and constructing approximately 3.8 miles of new circuit on steel monopoles configured for double circuit. | 2008-03-15 |  |  | 3124268 | [5 empty] | 115 | 9.5 | 954 ACSR, single conductor, double circuit | 65' to 75' galvanized steel structures. Some will be H-Frame replacements, new construction will be monopole structures double circuit capable. | 100 | 5.7 | 50 | 3.8 | 33397 | TRC Solutions still attempting to finalize easement requirements. Burns & McDonnell will schedule contractor once all easement requirements have been completed. | 3124268 | 0 | 3124268 | 2282101 |  | 3124268 | 0 | 0 | 5406369
TL110 | Dyer - Leo 115 kV Upgrade | El Paso, El Paso | Rebuild approximately 4.4 miles of 69 kV transmission line. EPE will replace existing structures and conductor. Existing 336 ACSR conductor will be replaced with 954 MCM ACSR and re-insulated for future 115 kV operation. A portion of the line passing through Ft. Bliss property will be realigned to accommodate plans for new housing development on the base. Consent for the relocation has been provided by the Directorate of Public Works, Ft. Bliss, Texas. | 2007-05-25 |  |  | 1200000 | 2419277 |  |  | 85% | 69 |  | 4.37 | 954 ACSR, single conductor, single circuit | 65'-90' steel monopole structures | Street ROW - franchise, 50 | 3.25, 1.14 | 50 | 1.12 | 25.101(c)(5)(B) |  | 2419277 | 0 | 2419277 |  |  | 2419277 | 0 | 0
TL107 | Dyer - Austin - 6400 Line 69 kV Rebuild | El Paso, El Paso | EPE will reconstruct and relocate approximately one mile of the existing Dyer - Austin 69 kV line. The line will be relocated to the existing 19400 Dyer-Austin 115 kV line which will be re-structured to accommodate the two circuits. Conductor on the existing 115 kV line will remain the same. 336 MCM ACSR conductor on the 69 kV line will be replaced with 954 MCM ACSR. The 69 kV line is being re-routed to minimize corners, guy poles and anchors in residential lots. The new route will also reduce interference with trees and improve reliability. System Planning has indicated the 69 kV line from Dyer - Austin will have to be reconductored by 2010 due to overloading. This project will complete approximately one-half of the required reconductor. | 2008-03-03 |  |  | 1057000 |  |  |  |  | 69 |  | 1 | 954 ACSR, single conductor, single circuit | one 105' steel H-Frame structure for freeway crossing, remaining structures are steel monopole double circuit tangents and self-supporting corner and dead-end structures. | 50 | 1 | n/a | n/a | 25.101(c)(5)(B), 25.101(c)(5)(C) | Foundation outside Dyer Substation will require variance from TXDOT. Documents being prepared, expect +/- 45 day turnaround. Construction tentatively scheduled for first of March. | 1057000 | 0 | 1057000 |  |  | 1057000 | 0 | 0
TL113 | Lane - Mann (6300 Line) Structure Replacement | El Paso, El Paso | EPE will replace 32 wood monopole structures along a 2.8 mile segment of line from Lane to Mann Substation. The structures are located along the access road (Gateway West) that parallells Intersatate 10. Over the years a number of structures have been replaced due to age and/or damage. This project will replace all remaining wood structures with steel. At least one if not two distribution circuits are attached to structures along this route. The new structures will accommodate existing distribution facilities. | 2008-03-03 |  |  | 266000 |  |  |  |  | 69 |  |  | 556 ACSR, single conductor, single circuit, center phase opposite, supported on davit arms and suspension insulators. | 85' galvanized steel monopole structures (74.5' AGL) configured for single circuit transmission with distribution underbuild (one and/or two circuits). | 50 | 2.8 | n/a | n/a | 25.101(c)(5)(B) | Awaiting confirmation of structure delivery times. | 266000 | 0 | 266000 | 2645259 |  | 266000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[18 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: |  |  | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[18 empty] | 12617430 | 100 | 4.92 |  |  | 0 | 0 | 13836707 | 13836707
[19 empty] | 2 | 2 |  |  |  | 0 | 6 | 6 | Project Count
[19 empty] | Completed | Active |  |  |  | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H2: Allen Steven Boling: $1,634,174 T-Line; $1,055,289 Substation
Note on H3: Allen Steven Boling: $5,335,988 T-Line; $568,230 Substation
Note on H4: Allen Steven Boling: $3,124,268 T-Line; $2,282,101 Substation
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AA7: Allen Steven Boling: ACTUAL FINAL COST

## FEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
#67102705 | KIOWA-TNMPC 69F138kV Transmission Line | Rains, Hunt | Rebuild 69 kV single wood pole and reconductor with 795 ACSR from Kiowa Substation to TNMPC Substation | 2006-02-02 | 2006-05-31 | na | 1243000 | 1740500 |  |  | 100 | 69 | 69 | 5.1 | 795 kcmil ACSR "Drake" | Single steel pole | 60 | 5.1 | 0 | 0 | 25.101( c)(5)( B)(i) | Project was never deenergized. Final costs have not been determined | 1740500 | 0 | 1740500 |  |  | 1740500 | 0 | 0
#67110105 | Forney - NW Terrell Transmission Line | Kaufman | New 138 kV transmission line from Windmill Farms Substation to TXU 138kV. | 2008-10-01 | 2009-07-01 |  | 2981000 |  |  |  | 0 | na | 138 | 5.06 | 795 kcmil ACSR "Drake" | Single steel pole | na | na | 80 | 5.06 | 28936 |  | 2981000 | 0 | 2981000 |  |  | 2981000 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 4721500 | 4721500
[24 empty] | 0 | 2 | 2 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## KELSON
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
KT-TX-01 | Canal-to-Deweyville | Chambers, Hardin, Jasper, Jefferson, Liberty, Newton, Orange | Install 345kV double-circuit line from proposed Canal Switching Station to the proposed Deweyville Switching Station, allowing connection of east Texas generation to ERCOT. | 2008-10-01 | 2010-04-01 |  | 268250000 |  |  |  | 0% | na | 345 | 190 | 2 per phase 795 kcmil ACSR | Tubular Steel monopole; double at some angles. | na | na | 120 - 150 | 95 | 34611 |  | 268250000 | 0 | 268250000 |  |  | #N/A | #N/A | #N/A
| THIS IS A PUC STAFF DRAFT BASED ON CCN APPLICATION INFORMATION. | [21 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
|  |  | 268250000 |  |  |  | T-Line: $255,945,000; Sw. Station: $12,425,000
|  |  | 268250000 |  |  |  | 255945000
|  |  | 12425000 |  |  |  | 12425000
|  |  | 280675000 |  |  |  | 268370000
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 268250000 | 268250000
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on D6: Allen Steven Boling: $268,250,000T Line; $12,425,000 Station ; TOTAL: $280,675,000
Note on H2: Allen Steven Boling: $268,250,000T Line; $12,425,000 Station ; TOTAL: $280,675,000

## LCRA
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
1001776, 1001840 | Kunitz-Wink | Culberson, Reeves, Loving, Winkler | New 138 kV transmission line from wind plant at Kunitz to TXU Wink Substation | 2009-06-05 | 2009-11-01 |  | 30212829 |  |  |  | 0% |  | 138 | 101.5 | 3x2-795 kcmil ACSR "Drake" | Single Pole & H-frame | na | 0 | 100 - 160 | 101.5 | CCN Docket No. 22762 approved 7/13/01 |  | 30212829 | 0 | 30212829 |  |  | 30212829 | 0 | 0
1005925 | Menger Creek Substation Addition Project (Cico-to-Helotes TL Addition T-244) | Kendall, Bexar, City of Boerne | Construct a new bundled 795 ACSR 138 kV transmission line approximately 4 miles in length from a tap point on the Boerne Cico-to-Helotes transmission line to the proposed Menger Creek Substation. | 2006-09-28 | 2007-06-22 | 2007-06-22 | 4551900 | 6569000 |  |  | 100% | na | 138 | 3.8 | 3x2-795 kcmil ACSR "Drake" | Single Pole, Steel or Prestressed Concrete | na | 0 | 80 | 3.8 | CCN Docket #29684 approved 3/22/06 |  | 6569000 | 0 | 6569000 |  |  | 6569000 | 0 | 0
1006537 1006536 | Friendship-to-Escarpment T363 Add Escarpment-to-Manchaca T420 Add | Hays, Travis | Construct new 138 kV transmission line from Friendship to Manchaca Subs, New Substation near Highway 45 | 2007-02-16 | 2009-01-31 |  | 14954446 | 19489000 |  |  | 50% | NA | 138 | 7.8 | 3x1-795 kcmil ACSR | SINGLE POLE, STEEL OR CONCRETE | NA | NA | 80 | 7.8 | STM Docket #30833 approved 8/23/05 | 3700 FEET ACROSS CIRCLE C GOLF COURSE WILL BE UNDERGROUND. Tranferred from PEC Docket No. 18389 | 19489000 | 0 | 19489000 |  |  | 19489000 | 0 | 0
1003547 | Medina Lake-to-CPS Anderson TL Add T-460 | Bandera, Medina | New 138 kV transmisison line from Medina Lake Substation through proposed Miico Substation to CPS Energy Tie | 2008-09-01 | 2009-12-31 |  | 13897000 |  |  |  | 0% | 0 | 138 | 9 | 3x1-795 ACSR "Drake" | Single Pole & Lattice Tower | 0 | 0 | Varies, 60, 80-170 | 9 | CCN Docket #32934 | CCN filed 8/2/06 | 13897000 | 0 | 13897000 |  |  | 13897000 | 0 | 0
1007722 | Dump Hill-to-Dale T125 Add | Caldwell | Overhaul existing transmission line | 2007-04-09 | 2007-06-13 | 2007-06-13 | 200000 | 328900 |  |  | 100% | 69 | 69 | 7.75 | 3x1-4/0 ACSR "Penguin" | Single Pole & Wood H | Varies | 7.75 | 0 | 0 | N/A (Overhaul) |  | 328900 | 0 | 328900 |  |  | 328900 | 0 | 0
1003538 | Rim Rock-to-Goat Creek TL Add | Kerr County | New 138 kV transmisison line, single circuit between the existing Rim Rock Substation and the proposed Goat Creek Substation and double circuit between the proposed Goat Creek Substation and the existing Harper Road to Ingram transmission line. | 2009-06-01 | 2009-12-31 |  | 11740000 |  |  |  | 0% | 0 | 138 | 9 | 3x1 & 6x1-336 ACSR "Linnet" | Single Pole & Lattice Tower | 0 | 0 | Varies, 60-130 | 8 | CCN Docket #33844 | Filed at the PUC on 2/20/07. | 11740000 | 0 | 11740000 |  |  | 11740000 | 0 | 0
1006620 1006621 1006622 1007498 1008225 1008226 | Clear Spring/Zorn-to-Hutto TL Add | Guadalupe, Caldwell, Travis and Williamson counties, alternate routes include Hays County; municipalities potentially affected include Hutto, Pflugerville, Austin, Mustang Ridge, Niederwald, Lockhart and Martindale | New 345 kV double-circuit transmission line; Clear Springs/Zorn to Gilleland Creek to Hutto | 2010-03-01 | 2011-08-31 |  | 151500000 |  |  |  | 0% | 0 | 345 | 170 | 6x2-959 ACSS/TW "Suwannee" | Lattice Towers & Other | 0 | 0 | Varies, 100-160 | 85 | CCN Docket #33978 | Filed at the PUC on 3/20/07 | 151500000 | 0 | 151500000 |  |  | 151500000 | 0 | 0
1008508 | Lampasas-to-Adamsville-to-Evant TL Add | Lampasas and Coryell counties | Upgrade the portion of the existing 138 kV transmission line T-128 connecting the Lampasas, Adamsville, and Evant substations (approximately 26 miles) from 4/0 ACSR (84 MVA) to 795 ACSR (220 MVA). | 2007-10-01 | 2008-03-31 |  |  | 7830000 |  |  | 50% | 138 | 138 | 26 | 3 x 1-795 26/7 ACSR "Drake" | H-Frame | Varies; 100', CL | 26 | 0 | 0 | 25.101(C)(5)(B) |  | 7830000 | 0 | 7830000 |  |  | 7830000 | 0 | 0
1008924 | Paleface-to-Miller Creek T124 Add | Blanco, Hays, Travis | Transmission line overhaul, replace poles, cross arms, and x-braces | 2007-11-05 | 2007-12-01 | 2007-12-01 |  | 263611 |  |  | 100% | 138 | 138 | 17.03 | 3x1-336 ACSR "Linnet: | H-frame | Varies, 60-ft, 100-ft | 17.03 | 0 | 0 | 25.101(C)(5)(B) |  | 263611 | 0 | 263611 |  |  | 263611 | 0 | 0
1009092 | Waelder-to-Flatonia T513 Add | Fayette, Gonzales | Transmission line overhaul, replace poles, cross arms, and x-braces | 2007-11-26 | 2008-01-11 | 2008-01-11 |  | 266764 |  |  | 100% | 69 | 69 | 11.54 | 3x1-4/0 ACSR "Penguin" | H-frame | Varies, CL, 100-ft | 11.54 | 0 | 0 | 25.101(C)(5)(B) |  | 266764 | 0 | 266764 |  |  | 266764 | 0 | 0
1008932 | Kendall-to-Mountain Top T342 Add | Kendall and Blanco counties | Replace deteriorated poles, cross arms, and x-braces as necessary. | 2008-01-07 | 2008-03-28 |  |  | 733500 |  |  | 30% | 138 | 138 | 35.22 | 3x1-336 ACSR "Linnet: | H-frame | Varies | 35.22 | 0 | 0 | 25.101(C)(5)(B) | Overhaul | 733500 | 0 | 733500 |  |  | 815056 | -81556 | -81556
1008926 | Luling-to-Waelder T145 Add | Caldwell and Gonzales counties | Replace deteriorated poles, cross arms, and x-braces as necessary. | 2008-01-28 | 2008-03-07 |  |  | 208800 |  |  | 5% | 69 | 69 | 21.63 | 3x1-4/0 ACSR "Penguin" | H-frame | Varies | 21.63 | 0 | 0 | 25.101(C)(5)(B) | Overhaul | 208800 | 0 | 208800 |  |  | 197395 | 11405 | -70151
1008227 | Gilleland Creek-to-McNeil T147 Add | Travis County | Rebuild and reconductor existing transmission line McNeil-Gilleland Creek | 2008-03-01 | 2008-06-30 |  | 6978000 |  |  |  | 0% | 138 | 138 | 7.52 | 3x1-1433 ACSS/TW "Merrimack" | Poles, Towers | Varios, 100-ft | 7.52 | 0 | 0 | 25.101(C)(5)(B) |  | 6978000 | 0 | 6978000 |  |  | 6978000 | 0 | -70151
1009285 | Avery Ranch-to-Buttercup T386 Add | Williamson County | Extend existing Avery Ranch to Buttercup transmission line (T386) into new Kent Street Substation. Landowner crossed has given consent. | 2008-04-11 | 2008-09-30 |  | 615700 |  |  |  | 0% | 138 | 138 | 0.1 | 6x2-795 kcmil ACSR "Drake" | Poles | 0 | 0 | 100-ft | 0.05 | 25.101(C)(5)(A) | Landowner consents to project | 615700 | 0 | 615700 |  |  | #N/A | #N/A | #N/A
1008936 | San Saba-to-Goldthwaite T461 Add | San Saba and Mills counties | Transmission line overhaul, replace poles, cross arms, and x-braces | 2008-04-14 | 2008-06-21 |  | 765810 |  |  |  | 0% | 69 | 69 | 18.22 | 3x1-4/0 ACSR "Penguin" | H-Frame | Varies | 18.22 | 0 | 0 | 25.101(C)(5)(B) | Overhaul | 765810 | 0 | 765810 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 | 5578000 |  | #N/A | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 | 24267000 |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A |  | 1005709
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A |  | 745822
[23 empty] | 0 | 0 | 0 | 5578000 |  | #N/A | #N/A | #N/A |  | 259887 | Difference
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 251398914 | 251398914
[24 empty] | 0 | 15 | 15 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H7: Allen Steven Boling: $ 11,740,000 T Line; $5,578,000 Station
Note on H8: Allen Steven Boling: $ 151,500,000 T Line; $ 24,267,000 Station
Note on H36: Allen Steven Boling: $ 11,740,000 T Line; $5,578,000 Station
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AI9: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.

## MVEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
801145 | North Edinburg to West Edinburg 138kV Line Rebuild and Second Circuit | Hidalgo | 9.1 Miles 138kv Transmission Line | 2007-02-19 | 2007-07-05 | 2007-07-06 | 2600000 |  |  |  | 100% | 138 |  | 9.1 | 795 ACSS | Single pole - concrete pole | 25 | 5.5 |  |  | 29225 | Construction Complete | 2600000 | 0 | 2600000 |  |  | 2600000 | 0 | 0
1972336 | Kenaf Plant | Willacy | 6.5 Miles 138kv Transmission Line | Delayed - May not be built | Delayed - May not be built |  | 1550000 |  |  |  | 0% |  |  | 6.5 | 795 ACSR | Single pole - concrete pole with steel davit arms |  |  | 25 | 0.68182 | 19577 | Project inactive and closed. | 1550000 | 0 | 1550000 |  |  | 1550000 | 0 | 0
50001 | Doedyns to Gandy- New 138kV Line | Hidalgo | 10.67 Miles 138kv Transmission Line | 2007-01-08 | 31/12/07 |  | 7137500 | 7109500 |  |  | 0% | 138 |  | 10.67 | 795 ACSS | Single pole - concrete pole |  |  | 50 | 12 | 32775 | CCN Approved, Substation Cost:$3,562,000 | 7109500 | 0 | 7109500 |  |  | 7109500 | 0 | 0
50002 | West Edinburg to Palmhurst 138kV Line Rebuild | Hidalgo | 3.5 Miles 138kv Transmission Line | 15/09/07 | 31/12/07 |  | 1575000 |  |  |  | 0% | 138 |  | 3.5 | 795 ACSS | Single pole - concrete pole | 25 | 3.5 |  |  | 25.101(c)(5)(B) | Upgrading conductor from 559 AAAC-795ACSS | 1575000 | 0 | 1575000 |  |  | 1575000 | 0 | 0
50003 | Palmhurst to Merett 138kV Line Rebuild | Hidalgo | 4.2 Miles 138kv Transmission Line | 2008-01-02 | 2008-01-04 |  | 2205000 |  |  |  | 0% | 138 |  | 4.2 | 795 ACSS | Single pole - concrete pole | 25 | 4.2 |  |  | 25.101(c)(5)(B) | Upgrading conductor from 559 AAAC-795ACSS | 2205000 | 0 | 2205000 |  |  | 2205000 | 0 | 0
50004 | Merett to Pharr 138kV Line Rebuild | Hidalgo | 1.8 Miles 138kv Transmission Line | 2008-01-04 | 31/05/08 |  | 945000 |  |  |  | 0% | 138 |  | 1.8 | 795 ACSS | Single pole - concrete pole | 25 | 1.87 |  |  | 25.101(c)(5)(B) | Upgrading conductor from 559 AAAC-795ACSS | 945000 | 0 | 945000 |  |  | 945000 | 0 | 0
918995 | 2nd & Wisconsin 138kV Line Relocation- Palmhurst to Merett | Hidalgo | 1.8 Miles 138kv Transmission Line | 2007-11-12 | 2007-12-31 |  | 200000 |  |  |  | 100% | 138 |  | 0.3 | 795 ACSS | Single pole - concrete pole | 25 | 0.3 |  |  | 25.101(c)(5)(F)ii | Awaiting final project costs. | 200000 | 0 | 200000 |  |  | 200000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[7 empty] | 7137500 | 7137500
The estimated cost for the proposed project is approximately $10,671,500. The estimated Transmission Line and substation costs are $7,109,500 and $3,562,000, respectively.
1 new project
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 16184500 | 16184500
[24 empty] | 0 | 7 | 7 | Project Count
[24 empty] | Completed | Active | Total
Note on H4: Allen Steven Boling: MVEC revised the cost ($6.6 MM) in the original application to $7.137500 MM in the Amended Application. Following the initial entry of $6.6 MM on the first report (T-Line only), MVEC entered $7.109,500 as the NEW Initial Estimated Project Cost. However, this would correctly be the cost in the Amedned Application, and not the new cost after routing adjustments had been made as a result of settlement. STAFF HAS THEREFORE CHANGED THE COST BACK TO $7.137500 AS STATED IN THE AMENDED APPLICATION.
Note on H17: Allen Steven Boling: MVEC revised the cost ($6.6 MM) in the original application to $7.137500 MM in the Amended Application. Following the initial entry of $6.6 MM on the first report (T-Line only), MVEC entered $7.109,500 as the NEW Initial Estimated Project Cost. However, this would correctly be the cost in the Amedned Application, and not the new cost after routing adjustments had been made as a result of settlement. STAFF HAS THEREFORE CHANGED THE COST BACK TO $7.137500 AS STATED IN THE AMENDED APPLICATION.
Note on I4: Allen Steven Boling: Final Estimated Cost: T Line: $7,109,500 Substation: $3,562,000
Note on I17: Allen Steven Boling: Final Estimated Cost: T Line: $7,109,500 Substation: $3,562,000

## PEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
02-WO8784 | BUDA TO LEHIGH REBUILD | BUDA,HAYS COUNTY | UPGRADE THE 69KV LINE TO 69/138KV FROM BUDA SUBSTATION TO THE NEW LEHIGH SUBSTATION | 2007-03-15 | NA | NA | 2270000 | 2800000 |  |  | 99% | 69 | 69, 138 | 7.00 mi | 795 ACSR DRAKE, SINGLE AND BUNDLE | SINGLE POLE, STEEL OR CONCRETE | 40, 60, 80 | 3.5 | 150 | 0.057 | 25.101(C)(5)(B), 25.101(C)(5)(C) | Fiber from Buda to Lehigh is not completed. | 2800000 | 0 | 2800000 |  |  | 2800000 | 0 | 0
02-WO8776 | LEHIGH TO KYLE REBUILD | KYLE, HAYS COUNTY | UPGRADE THE 69KV LINE TO 138KV FROM THE NEW LEHIGH SUBSTATION TO THE KYLE SUBSTATION | 2007-08-01 | NA | NA | 4035000 |  |  |  | 95% | 69 | 138 | 5.80 mi | 795 ACSR DRAKE, BUNDLE | SINGLE POLE, STEEL OR CONCRETE | 20 - 60 | 5.8 | NA | NA | 25.101(C)(5)(B) |  | 4035000 | 0 | 4035000 |  |  | 4035000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | 0 | 0 | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 6835000 | 6835000
[24 empty] | 0 | 2 | 2 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## GSEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
TX04560126 | Kelton Tap to Kelton Sub | Wheeler | New line from Kelton Tap to the new Kelton Sub. Built in public ROW. Contains distribution underbuild. | 2008-03-01 | 2008-05-15 |  | 3415000 |  |  |  | 0% |  | 69 | 18.4 | 477 mcm 27/7 ACSR | Monopole; Horizontal post insulators | 0 | 0 | Not specified; in public ROW | 18.4 (shares public ROW) | 34718 | Application filed 09/24/07. Only 1 route filed. Approved January 2008. | 3415000 | 0 | 3415000 |  |  | 3415000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[7 empty] | 3415000 | [20 empty] | #N/A | #N/A | #N/A
1615000
5030000
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 3415000 | 3415000
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on H2: Allen Steven Boling: T-Line: $3,415,000; Substation: $1,615,000; Total: $5,030,000
Note on I6: Allen Steven Boling: T-Line: $3,415,000; Substation: $1,615,000; Total: $5,030,000

## RCEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
#160121507 | RCEC 138kV Interconnect | Henderson & Van Zandt | New 138 kV transmission line from Barton Chapel Sw. to Ben Wheeler Sw. | 2008-11-01 | 2009-07-01 |  | 5689837 |  |  |  | 0 | na | 138 | 10.7 | 795 kcmil ACSR "Drake" | Single pole | na | na | 100 | 10.7 | 32707 |  | 5689837 | 0 | 5689837 |  |  | 5689837 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 5689837 | 5689837
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on H2: Allen Steven Boling: $5,689,837 T Line; $3,314,874 Station ; TOTAL: $9,004,711

## SHECO
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
| Enstor Transmission Line and Switching Station | Liberty | To serve the Enstor gas storage facility substation owned by Enstor | 2008-09-01 | 2008-12-01 | 2009-01-01 | 981531 |  |  |  | 0% | n/a | 138 | 1.96 | 795 kCM ACSR Drake | TU-1 Steel or concrete w/davit arms | n/a | n/a | 100 | 1.96 | 34650 |  | 981531 | 0 | 981531 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[7 empty] | T-Line: $981,531; Station work: $1,332,000 | [15 empty] | T-Line: $981,531; Station work: $1,332,000 | 0 | T-Line: $981,531; Station work: $1,332,000
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 981531 | 981531
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on H2: Allen Steven Boling: T-Line: $981,531; Station work: $1,332,000 Total: $2,313,531
Note on H11: Allen Steven Boling: T-Line: $981,531; Station work: $1,332,000 Total: $2,313,531

## SPS
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost ($) | Final Estimated Project Cost ($) | Final Actual Project Cost ($) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
10632305, 10761041, 10772756, 10772728 | Amarillo South to Spring Draw 115 kV project | Randall County, Texas | Aproximately 6 miles of new 115 kV transmission line from Amarillo South Interchange to a new 25 MVA distribution substation to be named Spring Draw, with a breaker terminal at Amarillo South Interchange | 2008-04-01 | 2008-06-01 |  | 5713557 |  |  |  | 45% |  | 115 | 6 | 397.5 MCM ACSR | Single-Pole Steel | NA | NA | 60 | 6 | 33602 |  | 5713557 | 0 | 5713557 |  |  | 5713557 | 0 | 0
10458573, 10497800, 10497813 | Cox Interchange to Floyd County Interchange 115 kV Transmission Project | Floyd & Hale County, Texas | Approximately 20 miles of new 115 kV transmission line from Cox Interchange to Floyd County Interchange, with a breaker terminal at Cox Interchange | 2008-01-01 | 2008-06-01 |  | 9898838 |  |  |  | 45% |  | 115 | 18.6 to 21.2 | 397.5 MCM ACSR | Single-Pole Steel or Concrete | 30 | 18.6 | 70 | 18.6 to 21.2 | 33456 |  | 9898838 | 0 | 9898838 |  |  | 5713557 | 4185281 | 4185281
10999406 |  |  | Replace polymer insulators on 345 kV circuit J-02 between Tolk Station near Muleshoe, Texas and Eddy County Interchange located near Artesia, New Mexico. | 2007-12-10 | 2008-02-08 |  | 1200000 |  |  |  | 100% | 345 Kv |  | 157 | 795 MCM Bundled | Wood "H" Frame | 100 | 157 |  |  |  | We are changing polymer insulators that have a common failure mode. We have experienced multiple failures during the past several years resulting in outages. We plan to replace all insulators at different intervals between December 10th and late February. | 1200000 | 0 | 1200000 |  |  | 5713557 | -4513557 | -328276
10956359, 10930322, 10930316, 11000417 | Mustang Station to Seminole Interchange 230 kV Project | Gaines & Yoakum County, Texas | Aproximately 18 miles of 230 kV transmission line from Mustang Station to Seminole Interchange. | 2009-02-02 | 2009-06-01 |  | 10320436 |  |  |  | 0% |  | 230 kV | 18 | 795 kcmil, ACSR | Single-pole self supporting steel | NA | NA | 90 | 18 | 35106 |  | 10320436 | 0 | 10320436 |  |  | 5713557 | 4606879 | 4278603
[20 empty] | 0 |  |  | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[20 empty] | 0 |  |  | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[20 empty] | 0 |  |  | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
0
123
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 27132831 | 27132831
[24 empty] | 0 | 4 | 4 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H5: Allen Steven Boling: T-Line: $10,320,436; Substation: $10,579,805; Total: $ 20,900,241
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## STEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) | sort | Last Month: | Current minus last month: | Cumulative Sum
700.2393 8002392 | Nursery Breakers | Victoria | Install 2 69 kV Breakers and Comm. | 12/2000 | 9/2006 |  | 400000 | 400000 |  |  | 100% | 69 | [8 empty] | 25.83(a)(3) | Waiting on accounting for close out. | 400000 | 0 | 400000 |  | 1 | 400000 | 0 | 0
705.2026 | Red Bluff 138/12 kV Substation | Jackson | Build 138/12 kV Substation | 7/2005 | 9/2006 |  | 1477000 |  |  |  | 100% | 138 | [8 empty] | 25.101 (c)(2) | Waiting on accounting to close out. | 1477000 | 0 | 1477000 |  | 2 | 1477000 | 0 | 0
704.2056 | Verdi 69/12 kV Substation | Wilson | Build 69/12 kV Substation | 7/2005 | 12/2007 |  | 330000 |  |  |  | 16% | 69 | [8 empty] | 25.101 (c)(2) | Oh hold. Public Mtg wont be held until the County Updates their tax roles. | 330000 | 0 | 330000 |  | 3 | 330000 | 0 | 0
705.1150, 705.6148, 702.2151 | Clay West 69/12 kV Substation | Live Oak | Build 69/12 kV Substation | 2007-02-01 | 7/2007 | 2007-07-10 | 390000 |  |  |  | 100% | 69 | [8 empty] | 25.101 (c)(2) | Waiting on accounting for close out. | 390000 | 0 | 390000 |  | 4 | 390000 | 0 | 0
705.2194 | Hilje 69/12 kV Substation | Wharton | Build 69/12 kV Substation | 11/2005 | 9/2007 |  | 330000 |  |  |  | 98% | 69 | [8 empty] | 25.101 (c)(2) | Dress out transformer and complete testing. | 330000 | 0 | 330000 |  | 5 | 330000 | 0 | 0
706.4067, 706.1069 | Botines 138/24 kV Substation | Webb | Build 138/24 kV Substation | 2006-07-01 | 2007-12-01 |  | 1480000 |  |  |  | 10% |  | 138 | [7 empty] | 25.101 (c)(2) | On hold until landowner signs easement. | 1480000 | 0 | 1480000 |  | 6 | 1480000 | 0 | 0
706-2068 | Botines 138 kV Transmission Line | Webb | Build 138 kV Transmissin Line to Botines Sub from AEP Laredo Switching Station | 2006-07-01 | 2007-12-01 |  | 1640000 |  |  |  | 7% |  | 138 | 0.9 | Single 795 ACSR | Wood or concrete pole |  |  | 80 | 0.9 | 25.101(c)(5)(A)(I) | On hold until landowner signs easement. | 1640000 | 0 | 1640000 |  | 7 | 1640000 | 0 | 0
705.203 | San Miguel to Lobo 345 kV Line | Atascosa, LaSalle, McMullen, Webb | Build 345 kV Line from San Miguel switching station to new Lobo switching station | 2/2007 | 4/2010 | 4/30/2010 | 48015600 |  |  |  | 23% |  |  | 42.4 | Two 1590 kcmil ACSR, bundle | Steel Monopole |  |  | 150 | 42.6 | 33033 | Soil borings are underway. Control points have been completed . Aerial photography can now begin. | 48015600 | 0 | 48015600 |  | 8 | 48015600 | 0 | 0
799.2089, 799.2087, 899.2088 | Pt. O'Connor to Union Carbide 69 kV Line | Calhoun | Build 69 kV line to Loop Pt. O'Connor and Seadrift Substations | 1/2007 | 08/2007 |  | 7440812 |  |  |  | 25% |  | 69 | 23.96 | Single 795 ACSR | Concrete pole | 50 | 4.22 | 50 | 19.74 | 32406 | Acquiring Right-Of-Way Easements | 7440812 | 0 | 7440812 |  | 9 | 7440812 | 0 | 0
707.222 | Palo Duro Substation | Frio | Build 138/12.kV Substation | 7/2007 | 12/2008 |  | 2200000 |  |  |  | 3% |  | 138 | [7 empty] | 25.101( c )(2) | Negotiation of site is in progress. | 2200000 | 0 | 2200000 |  | 10 | 2200000 | 0 | 0
707.2219 | Palo Duro to Dilley 138 kV Line | Frio | Build 69 kV & 138 kV double circuit line existing Dilley 138 kV Sub to new Palo Duro Sub | 7/2007 | 12/2008 |  | 4800000 |  |  |  | 1% |  | 138 | 13 | Single 795 ACSR (new) and single #4/0 ACSR (old) | Concrete pole | 40 | 13 | 100 | 13 | 25.101( c ) 5( C ) | Identifying landowners | 4800000 | 0 | 4800000 |  | 11 | 4800000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  | 12 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 13 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 14 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 15 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 16 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 17 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 18 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 19 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 20 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  | 21 | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[6 empty] | 0 | 0 | [15 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 68503412 | 68503412
[24 empty] | 0 | 11 | 11 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## SULP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
PR.04.05067.CAP | Sharyland HVDC Interconnect | Mission, Hidalgo County | Install 150 MVA back to back HVDC interconnection with CFE at SU's Railroad Substation. | 2005-04-01 | 2007-10-07 | 2007-10-07 | 37038398 | 39000000 |  |  | 100 | na | 138 kV | 0.8 | 795 acss single conductor | Concrete or Steel Poles | na | na | 80 | 0.8 | 28834 | Commissioned on 10/10/2007 | 39000000 | 0 | 39000000 |  |  | 39000000 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[25 empty] | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 39000000 | 39000000
[24 empty] | 0 | 1 | 1 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H2: Allen Steven Boling: THIS ESTIMATE WAS ENTERED BY PUC STAFF. TRANSMISSION LINE COST ESTIMATE $397,099 AND CONVERTER COST ESTIMATE $36,641,299 WERE BOTH ENTERED.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## SWEPCO
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
40030820 | Winnsboro to N. Mineola | Wood | Construct approximately 25 miles of new 138kV transmission line using single pole with davit arm construction. | 2007-01-08 | 2007-10-17 | 2007-10-17 | 9963000 | 17744565 |  |  | 100 | na | 138 | 25 | 1590 ACSR with Static | single pole steel or concrete with davit arms | na | na | 100 | 25 | 30128 & 31427 | Docket No. 31427 approved Preferred Route 9/8/05. | 17744565 | 0 | 17744565 |  |  | 17744565 | 0 | 0
TP-2006-130 | NW Texarkana to Bann Rebuild and Reconductor | Bowie | Reconductor and rebuild approximately 2.7 miles of the existing 4.3-mile 138KV transmisison line using single pole davit arm construction | 2007-11-15 | 2008-05-01 |  |  | 3344000 |  |  | 50 | 138 | 138 | 2.7 | 1590 ACSR with Static | single pole steel or concrete with davit arms | 100 | 2.7 | 0 | 0 | SUB.Rule 25.101 (c) (5) (B) |  | 3344000 | 0 | 3344000 |  |  | 3344000 | 0 | 0
TP-2007-161 | Sand Springs POD | Wood | Set dead-end structures in existing easement for 138KV loop into the new Wood County Electric Cooperative's Sand Springs substation. | 2008-09-15 | 2008-10-07 |  |  | 750377 |  |  |  | 138 | n/a | n/a | 1272 | concrete | 100 | n/a | n/a | n/a | SUB.Rule 25.101(c)(5)(A) | No New ROW required. Deadends set in exsting ROW. | 750377 | 0 | 750377 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 21838942 | 21838942
[24 empty] | 0 | 3 | 3 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## TNMP
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost (Total) | Final Estimated Project Cost (Total) | Final Actual Project Cost (Total) | % Variance | Percent Complete | Existing Voltage (kV) | Upgraded or New Voltage (kV) | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) | REQUESTED ADDITIONAL INFORMATION | Last Month: | Current minus last month: | Cumulative Sum
NTE07507 Y0015285 | County Road 101 | Reeves County, Texas | Build radial 138 kV line to serve Enterprise Products Operating L.P. | 2007-10-29 | 2008-02-05 | 2008-02-05 | 715856 | 722000 |  |  | 100% | 138 | 138 | 1.23 | 477 ACSR | Wooden H-Frame | na | na | 100 | 1.23 | 34294 | OCT 19, 2007 - PUC Approved CCN | 722000 | 0 | 722000 |  |  | 722000 | 0 | 0
STE07107 Y0012325 | Texas City 69F Relocation | Texas City, Texas | Relocate 1.4 miles of 69 kV transmission line out of the BP Refinery at the request of BP. | 2008-03-01 |  |  | 2744731 |  |  |  | 0% | 69 | na | 1.4 | 795 ACSR | Concrete | na | na | 40 | 1.4 | Rule 25.101(c)(5),(D) | BP is funding the cost of the project to remove the transmission line from the refinery. BP is furnishing easement in the greenbelt space adjacent to the refinery. Estimated start of construction has been delayed to March 2008 at the request of BP. This project involves minor modification of the existing 138kV line and 69kV distribution underbuild. | 2744731 | 0 | 2744731 |  |  | 2744731 | 0 | 0
NTE07207 | Interconnection between Sherbino I Wind Farm LLC and TNMP | Pecos County, Texas | Sherbino Mesa Wind Firm/White Baker to Rio Pecos Line Uprate project | 2008-09-18 |  |  | 8800000 |  |  |  | 0% | 138 | na | 14 | 795 ACSS | Wooden H-Frame | 70 | 14 | na | na | Rule 25.101(c)(5)(B),(D) | Initial commercial operation for the first 150 MW is expected by September 18, 2008 which corresponds with TNMP system improvements. The second 150 MW is scheduled for completion no later than July 10, 2010 to correspond with completion of improvements on AEP's system | 8800000 | 0 | 8800000 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[28 empty] | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 12266731 | 12266731
[24 empty] | 0 | 3 | 3 | Project Count
[24 empty] | Completed | Active | Total
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## TXU
Utility Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Sort | Last Month: | Current minus last month: | Cumulative Sum
00T64047 WB | North Herty-East Lufkin 138 kV: Thermal Upgrade Project | City of Lufkin, Angelina County | Replace the existing 795 kcmil ACSR conductor clamps and deadends with AGS units and compression deadends for high temperature operation, from North Herty Sub to the Tap. Relocate 5 existing lattice steel towers (NH-Tap). Rebuild wood H-frames on single steel poles from Tap to Junction (east of Lufkin East Sub). Replace 5 existing steel pole structures from LE Sub to Junction. Transfer existing 795 kcmil ACSR conductor and shield wire from Tap, to Junction, to LE Sub. | 2007-10-29 | 2008-12-19 | 2007-12-19 | 2498000 | 2498000 |  |  | 100 | 138 | na | 9.5 | 795 kcmil ACSR | Steel Poles and Lattice Towers | 100 | 9.5 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 2498000 | 0 | 2498000 |  |  | 1 | 2498000 | 0 | 0
04T62069 JB/EH | Euless - Bedford 138kV: Rebuild | City of Keller, Tarrant County | Rebuild 3.0 miles of existing double circuit 1033.5 kcmil ACSR conductor on steel poles and steel towers with bundled 1033.5 kcmil ACSR on steel poles. | 2006-05-17 | 2007-10-30 | 2007-10-30 | 1350000 | 1350000 |  |  | 100 | 138 | na | 6 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 3 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 1350000 | 0 | 1350000 |  |  | 2 | 1350000 | 0 | 0
05T62155 DRC | Alvarado-Hillsboro 69 kV Line: Replace Structures 132 and 133 | Hill County | Remove two existing 69 kV steel towers and install two 138 kV single poles due to severe erosion at Structure 133 | 2008-01-09 | 2008-01-10 |  | 90000 | 90000 |  |  | 100 | 69 | na | 0.4 | #1 Copper | Steel or Concrete Poles | 100 | 0.4 | na | na | 25.101(c)(5)(B) |  | 90000 | 0 | 90000 |  |  | 3 | 90000 | 0 | 0
05T62149 JB/EH | Colleyville Tap - Keller South (BEC) 138 kV: Rebuild | City of Fort Worth, Tarrant County | Rebuild 3.0 miles of existing double circuit 1033 kcmil ACSR conductor on steel towers and steel poles with 1926.9 kcmil ACSS/TW on steel poles. | 2006-06-19 | 2007-11-01 | 2007-11-01 | 4132000 | 4132000 |  |  | 100 | 138 | na | 6 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 3 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 4132000 | 0 | 4132000 |  |  | 4 | 4132000 | 0 | 0
05T62150 JB/EH | Keller South (BEC) - Keller Magnolia Tap 138 kV: Rebuild | City of Fort Worth, Tarrant County | Rebuild 2.3 miles of existing double circuit 1033 kcmil ACSR conductor on steel towers and steel poles with 1926.9 kcmil ACSS/TW on steel poles. | 2006-06-19 | 2007-11-01 | 2007-11-01 | 2989000 | 2989000 |  |  | 100 | 138 | na | 4.6 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 2.3 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 2989000 | 0 | 2989000 |  |  | 5 | 2989000 | 0 | 0
06T61001 SEI/BW | Sulphur Springs Switch-Sulphur Springs Substation 138 kV: Relocate structure 2/7 | City of Sulphur Springs, Hopkins County | Replace and relocate existing single circuit 138 kV concrete pole structure 60' north of the present location. | 2007-10-01 | 2007-10-09 |  | 72659 | 72659 |  |  | 100 | 138 | na | 0.18466 | 1590 kcmil ACSR | Concrete Pole | 100 | 0.18466 | na | na | 25.101(c)(5)(F) | Relocation is at the request of TxDOT and is 100% reimbursable by TxDOT. Final costs accumulating | 72659 | 0 | 72659 |  |  | 6 | 72659 | 0 | 0
05T64193 JE/BW | Temple - Troy 69 kV: Rebuild | City of Temple, Bell County | Rebuild 6.1 miles of the 9.3 mile Temple-Troy 69 kV line section with double circuit structures and with one circuit in place for operation at elevated temperature | 2007-01-22 | 2007-05-24 | 2007-05-24 | 4200000 | 4200000 |  |  | 100 | 69 | na | 6.1 | 795 kcmil ACSR | Steel Pole | Varies | 6.1 | na | na | 25.101(c)(5)(B) |  | 4200000 | 0 | 4200000 |  |  | 7 | 4200000 | 0 | 0
05T65310 JO/SEI | Payne-Gainesville 138kV: Connect GCEC Whitesboro SE Substation | City of Whitesboro, Grayson County | This project consists of installing line sectionalizing switches in the Whitesboro - Payne 138 kV Transmission Line to provide a point of interconnection (POI) for Grayson - Collin Electric Cooperative (GCEC) adjacent to the Oncor Electric Delivery's Whitesboro Southeast Substation | 2007-09-24 | 2007-10-05 | 2007-10-05 | 174943 | 174943 | 305676 |  | 100 | 138 | na | na | 1233 kcmil ACSS/TW | Steel H-Frame | na | na | na | na | 25.101(c)(5)(A) | Complete, waiting on customer to energize. Final cost reported FEB 08 will remove in MAR 08 | 174943 | 174943 | 0 |  |  | 8 | 174943 | 0 | 0
06T64022 MK/BW | Belton-Ft. Hood 138 kV Line: Rebuild the Belton-South Harker Heights section | City of Belton and City of Harker Heights, Bell County | This project consists of rebuilding 11.9 miles between Belton and South Harker Heights with 1590 kcmil ACSR on new double circuit steel pole structures with one circuit in place. | 2007-03-29 | 2007-11-20 | 2007-11-20 | 6024455 | 6024455 |  |  | 100 | 138 | na | 11.9 | 1590 kcmil ACSR | Steel Pole | na | 11.9 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 6024455 | 0 | 6024455 |  |  | 9 | 6024455 | 0 | 0
06T65018 BM/WB | Forney - Lake Hubbard 138 kV: Raise Span for High Temp Operation | Kaufman County | The project scope is to upgrade the 7.5-mile Forney – Lake Hubbard 138 kV Transmission Line for high temperature operation. This work will be done in two phases. The first phase will include replacing existing dead-ends with new compression dead-ends and installing one new concrete pole and the second phase will include replacing two existing 1200 Amp switches and switch structures. New 'H" frame type switch structures will also be installed. No new ROW will be required. | 2006-04-06 | 2008-05-15 |  | 412179 | 412179 |  |  | 70 | 138 | na | 7.58 | 795 kcmil ACSR 1431 kcmil ACSR | Steel Towers, Steel Poles and Concrete Poles | 175 | 7.58 | na | na | 25.101(c)(5)(B) | The Final Estimated Project Cost for this project will be updated when cost information for the second phase of the project becomes available later this year. Switch work on hold. | 412179 | 0 | 412179 |  |  | 10 | 412179 | 0 | 0
05T65379 BJP/BW | Parkdale-Medill St. 138 kV: DART SE-2 Relocation | City of Dallas, Dallas County | This project consists of relocating seven existing steel tower structures with seven self-supporting steel poles in order to accommodate DART's proposed SE-2 railway project. | 2007-06-01 | 2007-07-30 | 2007-07-30 | 700402 | 700402 |  |  | 100 | 138 | na | 1 | 795 kcmil ACSR | Steel Poles | na | na | Centerline Easement | 0.5 | 25.101(c)(5)(F) | The existing transmission line is in DART right-of-way and will remain in DART right-of-way after the relocation. Final costs accumulating. | 700402 | 0 | 700402 |  |  | 12 | 700402 | 0 | 0
07T64028 MK/BW | Lake Creek-West Waco 138 kV: Install New Northwest Robinson Substation | City of Robinson, McLennan County | This project consists of replacing one existing wood H-frame and transferring conductors and shield wires in order to accommodate the installation of the Northwest Robinson Substation. | 2008-01-07 | 2008-01-08 |  | 50000 | 50000 |  |  | 100 | 138 | na | na | 336.4 kcmil ACSR Bundled | Concrete H-Frame | 100 | na | na | na | 25.101(c)(5)(A) |  | 50000 | 0 | 50000 |  |  | 13 | 50000 | 0 | 0
06T65197 MM/BP | Parkdale-Medill 138 kV: Relocate Structure T-310 | City of Dallas, Dallas County | Relocating structure T-310 in the Parkdale-Medill 138 kV Transmission Line due to an erosion problem. | 2007-06-11 | 2007-08-05 | 2007-08-05 | 131000 | 131000 |  |  | 100 | 138 | na | 0.01 | 400 kcmil Copper | Steel Towers | 100 | 0.01 | na | na | 25.101(c)(5)(E) | Final costs accumulating. | 131000 | 0 | 131000 |  |  | 14 | 131000 | 0 | 0
06T65105 MH/BW | Allen Switch - Lavon 138 kV: Northwest Wylie Substation Line Switch Replacement Project | City of Wylie, Collin County | Replace the existing 138kV transmission line switch structure located at the Northwest Wylie Substation. | 2007-04-16 | 2007-04-27 | 2007-04-27 | 450000 | 450000 |  |  | 100 | 138 | na | na | 1926.9 kcmil ACSS/TW | Steel Pole | 150 | na | na | na | 25.101(c)(5)(B) | Final costs accumulating. | 450000 | 0 | 450000 |  |  | 15 | 450000 | 0 | 0
06T62073 DRC/EB | Venus-Sherry 345 kV: Rebuild | City of Arlington, Tarrant County | Add a second circuit of 959.6 ACSS/TW bundled conductor to the existing steel towers on the Cedar Hill - Venus 345 kV Transmission Line between the Webb Substation and the Century Tap. Remove the existing Century Tap and reconfigure to complete a 345 kV circuit between the Venus Switching Station and the Sherry Switching Station. | 2007-01-02 | 2007-04-14 | 2007-04-14 | 1330000 | 1330000 | 892892 |  | 100 | 345 | na | 1.4 | 959.6 ACSS/TW Bundled | Steel Poles and Steel Towers | 150 | 1.4 | na | na | 25.101(c)(5)(B) | Final cost reported FEB 08 will remove in MAR 08 | 1330000 | 1330000 | 0 |  |  | 17 | 1330000 | 0 | 0
06T65307 06T65308 JB/TW | Royse Switching Station - Terrell Switching Station 69kV/138kV Rebuild | City of Terrell and City of Royse City, Rockwall County, Hunt County and Kaufman County | Rebuild 16.0 miles of existing single circuit single 4/0 ACSR conductor on steel poles with single 1590 kcmil ACSR on steel poles. This new construction will be insulated for 138 kV. One circuit will operate at 69 kV and a new second circuit will operate at 138 kV. | 2006-05-30 | 2007-06-01 | 2007-06-01 | 9736464 | 10000000 | 22337600 |  | 100 | 69/138 | na | 33 | 1590 kcmil ACSR | Steel Poles | 100 | 16.5 | na | na | 25.101(c)(5)(B) | This project has been divided into two new WA's, 06T65307 and 06T65308. Final cost reported FEB 08 will remove in MAR 08 | 10000000 | 10000000 | 0 |  |  | 18 | 10000000 | 0 | 0
06T61007 SEI/BW | Royse Switching Station-Terrell Substation138/69 kV: Relocate structures 18/2 and 18/3 | City of Terrell, Kaufman County | Replace H-frame bottom section and relocate existing steel pole triple circuit H-frame structures. | 2007-08-01 | 2007-09-20 |  | 376885.8 | 376885.8 |  |  | 100 | 69/138 | na | 0.60985 | 1590 kcmil ACSR | Steel H-Frame | 100 | 0.30492 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 376885.8 | 0 | 376885.8 |  |  | 19 | 376885.8 | 0 | 0
06T61009 SEI/BW | Norwood-Denton-Bowie 138 kV: Relocate Structures 2/8, 3/1, 3/2, and 3/3 | City of Irving, Dallas County | Replace double circuit lattice towers with double circuit lattice towers and double circuit steel poles with anchor bolt foundations. | 2008-05-01 | 2008-05-21 |  | 721679 | 721679 |  |  | 0 | 138 | na | 1.5765 | 1033.5 kcmil ACSR | Steel Towers and Steel Poles | 100 | 0.78826 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. This project is deferred. Waiting on TxDOT approval. | 721679 | 0 | 721679 |  |  | 20 | 721679 | 0 | 0
06T64146 BW/BM | Palestine-Palestine ALCOA 138 kV: Replace and Relocate | Anderson County | This project is to replace these two deteriorating wood H-frame structures with two direct embedded, concrete H-frames approximately 10' from their existing locations. The existing 1033 kcmil ACSR conductor and the double 3/8" EHS shield wire will be reused. | 2007-10-15 | 2007-10-18 |  | 151333 | 235000 |  |  | 100 | 138 | na | 0.1 | 1033.5 kcmil ACSR | Concrete H-Frames | 100 | 0.1 | na | na | 25.101(c)(5)(B) |  | 235000 | 0 | 235000 |  |  | 21 | 235000 | 0 | 0
06T64145 BW/BM | Jewett-Crockett-Lufkin 138 kV: Replace and Relocate | Houston County | This project is to replace these two wood H-frame structures with two direct embedded, concrete H-frames. One new concrete H-frame will be approximately 100' from the existing location in the lake and the other new concrete H-frame will be approximately 10' from it's existing location. The existing single circuit 4/0 ACSR conductor and double 3/8" EHS shield wire will be reused. | 2007-10-10 | 2007-10-13 |  | 160382 | 245000 |  |  | 100 | 138 | na | 0.1 | 4/0 ACSR | Concrete H-Frames | 100 | 0.1 | na | na | 25.101(c)(5)(B) |  | 245000 | 0 | 245000 |  |  | 22 | 245000 | 0 | 0
06T63050 06T63042 JM/JO | Wink - N. Andrews 138KV-Switch Replacement # 2813 - 2815 | Winkler County | This project will involve replacing two 138 kV 1200 amp type LD switches, with new 2000amp type LDS air switches for the Cheyenne tap. One existing wood H-frame type switch structure will be replaced with two new H-frame switch structures and two wood tangent H-frames will be replaced on the Wink-North Andrews 138 kV Transmission Line. Additionally one tangent wood H-frame will be replaced with a new steel H-frame on the Cheyenne Tap. | 2007-06-11 | 2007-07-31 | 2007-07-31 | 537434 | 1400000 |  |  | 100 | 138 | na | 0.32 | 795 kcmil ACSR and 556.5 kcmil ACSR | Wood H-Frames and Steel H-Frames | 50 | 0.32 | na | na | 25.101(c)(5)(B) | Final cost accumulating. | 1400000 | 0 | 1400000 |  |  | 23 | 1400000 | 0 | 0
06T42516 BM/BW | South Marlin Tap 69 kV: Replace Switches #2012 and 2013 | City of Marlin, Falls County | This project will consist of removing three 69 kV 600 amp type LD switches and replacing them with two 1200 amp 69 kV switches. Also, included in this project will be to replace the existing motor operators with new self contained motor operators. The existing switch structure will be utilized although some modification will be required on the switch platform. | 2007-11-29 | 2007-12-01 | 2007-12-01 | 199000 | 265000 |  |  | 100 | 69 | na | 0.01 | 336.4 kcmil ACSR | Steel Tower | 50 | 0.01 | na | na | 25.101(c)(5)(B) |  | 265000 | 0 | 265000 |  |  | 24 | 265000 | 0 | 0
05T64098 BW/JM | Marlin-Groesbeck 69 kV: Relocate for Marlin Lake | City of Marlin, Falls County | A section of the Marlin - Groesbeck 69 kV line is currently running through Old Mill Lake with three wood H-frame structures within the lake boundaries. Five existing wood H-frame structures will be removed and four new structures will be installed such that all structures will be located outside of the lake. Two of the new structures will be direct embedded, concrete H-frames and two of the structures will be anchor bolt foundation, steel H-frames. This project will include removing approximately 2100' of single circuit 336.4 kcmil ACSR conductor and replacing with approximately 2100' of 795 kcmil ACSR. Also approximately 2100' of 3/8" EHS double shield wire will be replaced with 2100' of 7/16 EHS double shield wire. | 2007-03-19 | 2007-12-31 |  | 290951 | 290951 |  |  | 100 | 69 | na | 0.3977 | 795 kcmil ACSR | Concrete H-Frames and Steel H-Frames | 50 | 0.3977 | na | na | 25.101(c)(5)(B) |  | 290951 | 0 | 290951 |  |  | 25 | 290951 | 0 | 0
06T61018 SEI/BW | Benbrook-Mistletoe 138 kV: Relocate Structures 7/4 and 7/5 | City of Fort Worth, Tarrant County | Replace double circuit steel poles with double circuit steel poles supported by anchor bolt foundations. | 2008-05-01 | 2008-05-15 |  | 261484 | 261484 |  |  | 0 | 138 | na | 0.73097 | 1926.9 kcmil ACSS /TW | Steel Poles | 100 | 0.36549 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. This project is deferred. | 261484 | 0 | 261484 |  |  | 26 | 261484 | 0 | 0
06T61021 SEI/BW | Malakoff-Mabank 138 kV: Relocate Structures 12/1 and 12/2 | Henderson County | Replace wood single circuit H-frames structures with concrete single circuit H-frames structures. | 2007-04-10 | 2007-04-12 | 2007-04-12 | 158277 | 158277 | 1e-05 |  | 100 | 138 | na | 0.35871 | 336.4 kcmil ACSR | Concrete H-Frames | 100 | 0.35871 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. TxDOT has reimbursed ONCOR. Final cost reported FEB 08 will remove in MAR 08 | 158277 | 158277 | 0 |  |  | 27 | 158277 | 0 | 0
06T65253 BJP/BW | East Levee-Amelia 138 kV Line: DART NW1-B Relocation at Oaklawn | City of Dallas, Dallas County | This project consists of relocating one existing steel guy stub pole structure with one self-supporting steel guyed pole in order to accommodate DART's proposed NW1-B railway project at Oak Lawn Avenue. | 2007-07-13 | 2007-07-20 | 2007-07-20 | 220204 | 220204 |  |  | 100 | 138 | na | na | na | Steel Pole | na | na | na | na | 25.101(c)(5)(F) | The existing guy pole is in DART right-of-way and will remain in DART right-of-way after the relocation. | 220204 | 0 | 220204 |  |  | 28 | 220204 | 0 | 0
06T63025 DRC/EB | Midessa-Midland Airport 138 kV: Rebuild and Upgrade Capacity | Midland County | Rebuild the existing 138 kV circuit from Midessa Substation to Midland Airport Substation with 1590 kcmil ACSR, a distance of approximately 7.2 miles. Replace existing wood H-Frame structures with concrete H-Frames. | 2007-01-02 | 2007-10-26 |  | 2900000 | 3175000 |  |  | 100 | 138 | na | 7.2 | 1590 kcmil ACSR | Concrete Poles | 75 | 7.2 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 3175000 | 0 | 3175000 |  |  | 29 | 3175000 | 0 | 0
06T63083 DRC/EB | Odessa EHV-Odessa 138 kV: Reconductor | City of Odessa, Odessa County | Reconductor 138 kV circuit from Odessa EHV Switching Station to Odessa #2 Substation with 1590 kcmil ACSR, a distance of approximately 2.3 miles. | 2007-12-02 | 2007-12-11 | 2007-12-11 | 350000 | 350000 |  |  | 100 | 138 | na | 2.3 | 1590 kcmil ACSR | Steel and Concrete Poles | Varies: 75/50 | 2.3 | na | na | 25.101(c)(5)(B) |  | 350000 | 0 | 350000 |  |  | 30 | 350000 | 0 | 0
06T65294 DRC/YB | Commerce Sw.-Wolfe City 138 kV: Rebuild and Upgrade Capacity | City of Commerce, City of Wolfe City, Hunt County | Rebuild the existing 138 kV circuit from Commerce Switching Station to Wolfe City Substation with 795 kcmil ACSR, a distance of approximately 12.7 miles. Replace existing wood H-Frame structures with concrete and steel poles. | 2007-01-02 | 2007-05-20 | 2007-05-20 | 3000000 | 3100000 | 4035549 |  | 100 | 138 | na | 12.7 | 795 kcmil ACSR | Concrete and Steel Poles | 100 | 12.7 | na | na | 25.101(c)(5)(B) | Final cost reported FEB 08 will remove in MAR 08 | 3100000 | 3100000 | 0 |  |  | 31 | 3100000 | 0 | 0
06T61024 SEI/BW | Payne-Gainesville 69 kV: Relocate Structures 5/1, 5/2, 5/3 & 5/4 | City of Sherman, Grayson County | Replace single circuit wood H-frame structures with single circuit concrete H-frame structures. | 2007-05-21 | 2007-06-14 | 2007-06-14 | 266853 | 266853 | 1e-05 |  | 100 | 69 | na | 0.47348 | 3/0 ACSR | Concrete H-frames | 100 | 0.47348 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. Final cost reported FEB 08 will remove in MAR 08 | 266853 | 266853 | 0 |  |  | 32 | 266853 | 0 | 0
06T61023 SEI/BW | Payne-Gainesville 138 kV: Relocate Structure 5/2 | City of Sherman, Grayson County | Replace single circuit concrete H-frame structure with single circuit concrete H-frame structure. | 2007-06-18 | 2007-06-15 | 2007-06-15 | 104139 | 104139 | 1e-05 |  | 100 | 138 | na | 0.17704 | 1233.6 kcmil ACSS | Concrete H-frames | 100 | 0.17704 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. Final cost reported FEB 08 will remove in MAR 08 | 104139 | 104139 | 0 |  |  | 33 | 104139 | 0 | 0
06T61027 SEI/BW | E. Richardson-N. Mesquite 138 kV, PGBT @ Liberty Grove Rd.: Relocate Structures 14/3 & 14/4 | City of Rowlett, Dallas County | Relocate existing single circuit steel poles to new anchor bolt foundations. | 2008-10-15 | 2008-11-15 |  | 190920 | 190920 |  |  | 0 | 138 | na | 0.28277 | 1033.5 kcmil ACSR | Steel poles | 100 | 0.28277 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. This project is deferred. | 190920 | 0 | 190920 |  |  | 34 | 190920 | 0 | 0
06T61028 SEI/BW | E. Richardson-N. Mesquite 138 kV, PGBT @ Miller Rd.: Relocate Structures 15/8, 15/9, 15/10 & 16/1 | City of Rowlett, Dallas County | Replace single circuit steel tangent & deadend poles with new single circuit tangent & deadend steel poles with anchor bolt foundations. | 2008-10-15 | 2008-11-15 |  | 477933 | 477933 |  |  | 0 | 138 | na | 0.50379 | 795 kcmil ACSR | Steel poles | 100 | 0.50379 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by TxDOT. This project is deferred. | 477933 | 0 | 477933 |  |  | 35 | 477933 | 0 | 0
06T65142 TW/JE | Upgrade East Mesquite - West Mesquite 138 kV Line Section | Mesquite, Dallas County, TX | Reconductor using existing structures. Replace insulators, shield wire and conductors for operation at elevated temperature. | 2007-11-12 | 2007-12-06 | 2007-12-06 | 753368 | 753368 |  |  | 100 | 138 | na | 2.7 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 2.7 | na | na | 25.101(c)(5)(B) |  | 753368 | 0 | 753368 |  |  | 36 | 753368 | 0 | 0
06T64080 MK/BW | Temple-Lampasas 138 kV Line (Nolanville-Harker Heights Section) | City of Harker Heights, Bell County | This project consists of rebuilding 7 miles between Nolanville and Harker Heights 138 kV line with 1590 MCM ACSR on new double circuit steel pole structures with one circuit in place. | 2008-01-14 | 2008-04-15 |  | 3300000 | 3300000 |  |  | 20 | 138 | na | 7 | 1590 kcmil ACSR | Steel Poles | 100 | 7 | na | na | 25.101(c)(5)(B) |  | 3300000 | 0 | 3300000 |  |  | 37 | 3300000 | 0 | 0
07T64025 07T64026 MK/BW | Athens-Tyler West 69 kV Line, Elkton-Forest Grove 138kV Line | City of Athens, Henderson County | This project consists of rebuilding 1 mile between Athens Sub and Trinidad-Elkton 69 kava line with 795 MCM ACSR on new double circuit steel pole structures and adding a 138kv circuit extension. | 2008-03-15 | 2008-05-15 |  | 750000 | 750000 |  |  | 0 | 69 | 69 138 | 2 | 795 kcmil ACSR | Steel Poles | 100 | 1 | na | na | 25.101(c)(5)(B) 25.101(c)(5)(C) |  | 750000 | 0 | 750000 |  |  | 38 | 750000 | 0 | 0
05T65418 TW/FC | Gainesville-Muenster 69kV: Rebuild | City of Muenster, City of Gainesville, Cooke County. | This project consists of rebuilding 13.8 miles between Gainesville Dixon Street substation and Muenster substation 69 kV line with 336 kcmil ACSR conductor on single circuit concrete poles. | 2007-11-15 | 2008-05-15 |  | 9717669 | 9717669 |  |  | 15 | 69 | na | 13.8 | 336 MCM ACSR | Concrete Poles | na | na | na | na | 25.101(c)(5)(B) |  | 9717669 | 0 | 9717669 |  |  | 39 | 9717669 | 0 | 0
06T65310 TW/FC | NW Carrollton-Gainesville 138 kV: Replace two structures | City of Gainesville, Cooke County. | This project consists of replacing two wood H-frame structures with taller concrete H-frame structures on the NW Carrollton-Gainesville 138 kV line. This is needed for clearance on the Gainesville-Montague Co 69 kV line rebuild. | 2008-03-01 | 2008-05-01 |  | 100000 | 100000 |  |  | 0 | 138 | na | na | 795 kcmil ACSR | Concrete H-frames | na | na | na | na | 25.101(c)(5)(B) | Project built in conjunction with 05T65418 rebuild Gainesville-Muenster 69 kV line section. Project has been deferred. | 100000 | 0 | 100000 |  |  | 40 | 100000 | 0 | 0
06T62208 WB/JM | Lingleville-Stephenville 138 kV Line Rebuild | Erath County Texas | This project will rebuild the existing Lingleville-Stephenville 138 kV line to accommodate double circuit 959.6 ACSS/TW. This will include installing new double circuit structures. The new structures are as follows: 1 steel pole, 113, 0-1 degree concrete poles and 2 concrete H-frame structures. The new line will be approximately 14.4 miles in length per circuit. Only one circuit of the new 959.6 ACSS/TW will be installed at this time. Additionally, all existing wood H-frames and the existing 4/0 conductor will be removed. | 2007-07-01 | 2007-10-26 | 2007-10-26 | 8970483.2 | 8970483.2 |  |  | 100 | 138 | na | 14.4 | 959.6 kcmil ACSS/TW | Concrete poles, Steel poles and Steel H-frames | 100 | 14.4 | na | na | 25.101(c)(5)(B) | Final costs accumulating | 8970483.2 | 0 | 8970483.2 |  |  | 41 | 8970483.2 | 0 | 0
06T64076 BW/MH | Upgrade Seaway Teague - W. Fairfield 138kV line. | City of Teague, City of Fairfield, Freestone County | Upgrade the 13.0 mile Seaway Teague - W. Fairfield 138kV line. Using a single conductor 795 ACSR "Drake" conductor. | 2008-01-03 | 2008-05-15 |  | 8921916 | 8921916 |  |  | 20 | 138 | na | 13 | 795 kcmil ACSR | Steel Poles | 100 | 13 | na | na | 25.101(c)(5)(B) |  | 8921916 | 0 | 8921916 |  |  | 42 | 8921916 | 0 | 0
06T64226 BW/MH | Upgrade Jewett-Seaway Teague 138kv line | City of Jewett, Leon County City of Teague, Freestone County | Upgrade the 10.75 mile Jewett - Seaway Teague 138kV line. Using a single conductor 795 ACSR "Drake". | 2007-10-15 | 2008-01-17 | 2008-01-17 | 9060498 | 9060498 |  |  | 100 | 138 | na | 10.75 | 795 kcmil ACSR | Steel Poles | 100 | 10.75 | na | na | 25.101(c)(5)(B) |  | 9060498 | 0 | 9060498 |  |  | 43 | 9060498 | 0 | 0
06T61008 SEI/BW | Irving N.E.-Las Colinas 138 kV: Relocate Structures 1/1, 1/2, 1/3 and 1/4 | City of Irving, Dallas County | Replace double circuit steel poles and lattice towers with double circuit steel poles with anchor bolt foundations. | 2008-04-15 | 2008-05-01 |  | 344328 | 344328 |  |  | 0 | 138 | na | 0.78674 | 1033.5 kcmil ACSR | Steel Poles | 100 | 0.39337 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable. | 344328 | 0 | 344328 |  |  | 44 | 344328 | 0 | 0
07T61002 SEI/BW | N.E. Irving Tap 138 kV: Relocate Structure 1/10 | City of Irving, Dallas County | Replace existing double circuit steel pole with new double circuit steel poles with anchor bolt foundations. | 2008-04-15 | 2008-05-01 |  | 110769 | 110769 |  |  | 0 | 138 | na | 0.36894 | 1033.5 kcmil ACSR | Steel Poles | 100 | 0.18447 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable. | 110769 | 0 | 110769 |  |  | 45 | 110769 | 0 | 0
06T62077 JO | Forest Hill-Texas Steel 138kV: TRWD Substation (POI) | City of Fort Worth, Tarrant County | Installing line sectionalizing switches in the Rolling Hills Tap line to provide a Point of Interconnection (POI) for Tarrant Regional Water District (TRWD) Substation. | 2007-08-27 | 2007-11-30 |  | 203994.38 | 203994.38 |  |  | 100 | 138 | na | na | 336 kcmil ACSR | Steel H-Frame | 100 | 0.96 | na | na | 25.101(c)(5)(A) | Waiting on Customer to Energize and Complete. | 203994.38 | 0 | 203994.38 |  |  | 46 | 203994.38 | 0 | 0
07T61004 BW/MK | Rivercrest-Sulphur Springs 138kV Line | City of Sulphur Springs, Hopkins County | This project consists of replacing and raising three H-frame structures for the Thermo Mining operations at Monticello to allow sufficient clearance for hauling equipment. | 2008-05-01 | 2008-05-15 |  | 130000 | 130000 |  |  | 0 | 138 | na | 0.42 | 636 kcmil ACSR | Concrete H-Frame | na | na | na | na | 25.101(c)(5)(D) | This project is 100% reimbursable. Project deferred by Thermo Mining. | 130000 | 0 | 130000 |  |  | 47 | 130000 | 0 | 0
06T62200 EH | Oran-Graham 138 kV Line- Modify for Barton Switching Station | Young County | Remove one existing wood H-frame, and install concrete deadend angle structures to connect to new switching station. | 2007-04-27 | 2007-05-04 |  | 160000 | 160000 | 121608 |  | 100 | 138 | na | 7 | 636 kcmil ACSR | Concrete Poles | 50 | 0.05 | 50 | 0.05 | 25.101(c)(5)(A) | Final cost reported FEB 08 will remove in MAR 08 | 160000 | 160000 | 0 |  |  | 48 | 160000 | 0 | 0
07T63037 EH | Nylon Tap-Olefin-General Tire 138kV Line Re-build | Odessa, Ector County | Upgrade the Nylon Tap-Olefin-General Tire 138kV line from Olefin Tap to Olefin and from Olefin to General Tire (1.4 miles) to obtain a summer rating of 897 amperes. | 2007-11-05 | 2007-11-20 | 2007-11-20 | 352222 | 352222 |  |  | 100 | 138 | na | 1.4 | 795 kcmil ACSS | Concrete Poles and Steel Towers | Centerline Easement | 1.4 | na | na | 25.101(c)(5)(B) |  | 352222 | 0 | 352222 |  |  | 49 | 352222 | 0 | 0
07T61005 SEI/BW | Calmont-Mineral Wells 69kv:Relocate Structures 2/18, 2/19, and 2/20 | City of White Settlement, Tarrant County | Relocate and replace single circuit wood poles with single circuit concrete poles with direct embed foundations. | 2007-08-13 | 2007-11-20 | 2007-11-20 | 206339 | 206339 |  |  | 100 | 69 | na | 0.19697 | 3/8-7 EHS Shield, 556.5 ACSR Phase | Concrete Poles | Centerline Easement | 0.19697 | 100 | 0.30189 | 25.101(c)(5)(F) | Relocation is at the request of the White Settlement ISD and is 100% reimbursable by the White Settlement ISD. | 206339 | 0 | 206339 |  |  | 50 | 206339 | 0 | 0
07T61008 SEI/BW | Poage-Seaton 69kV:Relocate Structure 8/4 | City of Temple, Bell County | Replace existing single circuit wood H-frame structure with new single circuit wood H-frame structure with direct embed foundations. | 2008-04-01 | 2008-04-15 |  | 45000 | 45000 |  |  | 0 | 69 | na | 0.2197 | 3/8-7 HS Shield, 2/0 Type F, Copperweld-CU Phase | Wood H-frame | 100 | 0.2197 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 45000 | 0 | 45000 |  |  | 51 | 45000 | 0 | 0
07T61003 SEI/BW | Coppell-Apollo 69kV:Relocate Structure 14N-1W-172 and 14N-1W-173 | City of Dallas, Dallas County | Replace existing wood single circuit, single pole structures with new concrete single circuit, single pole structures with direct embed foundations. | 2008-05-01 | 2008-05-15 |  | 128505 | 128505 |  |  | 0 | 69 | na | 0.1178 | 3/8-7 EHS Shield, 4/0 ACSR Phase | Concrete Poles | 50 | 0.1178 | 50 | 0.13239 | 25.101(c)(5)(D) | Relocation is at the request of the property owner and is 100% reimbursable by the property owner. Project Deferred until 2008 | 128505 | 0 | 128505 |  |  | 52 | 128505 | 0 | 0
06T61015 SEI/BW | Wichita Falls-Dundee-Bomarton 69kV:Install 80 Structures and Remove 98 Structures | City of Seymour, Baylor County | Replace existing wood single circuit, single pole structures with new wood, concrete and steel single circuit, single pole structures with direct embed foundations. | 2007-07-16 | 2007-12-31 | 2007-12-31 | 976518 | 976518 |  |  | 100 | 69 | na | 5.3284 | 1/0 ACSR, 4/0 ACSR | Wood, Concrete and Steel Poles | Centerline Easement | 5.3284 | Centerline Easement | 5.3937 | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 976518 | 0 | 976518 |  |  | 53 | 976518 | 0 | 0
07T63046 DRC | Morgan Creek-Graham 345 kV Line - Changes for Tonkowa Sw. Station | Scurry County | This project covers the required transmission line changes required to connect the new Tonkowa Switching Station to the 345 kV grid. Tonkowa Sw. Station will be the interconnect point between Oncor Electric Delivery and AirTricity's Roscoe Wind Farm merchant generation facility near Roscoe, Texas. The general scope of the project will involve looping the existing 345 kV line into the new Tonkowa switching station. This work will involve relocating one lattice tower and the addition of two self supporting lattice steel tower structures, and the installation of approximately 400' linear feet of 2-1590 ACSR to the new station dead end structure. | 2007-10-01 | 2007-12-16 | 2007-12-16 | 400000 |  |  |  | 100 | 345 | na | 0.2 | 1590 kcmil ACSR Bundled | Steel Towers | 140 | 0.2 | na | na | 25.101(c)(5)(A) |  | 400000 | 0 | 400000 |  |  | 54 | 400000 | 0 | 0
07T63050 DRC | Midland East - Big Spring West 138 kV Line - Changes for Stanton East Sw. Station | Martin County | This project covers the required transmission line changes required to connect the new Stanton East Switching Station to the 138 kV grid. Stanton East Sw. Station will be the interconnect point between Oncor Electric Delivery and Stanton Invenergy Wind Generation merchant facility near Stanton, Texas. The general scope of the project will involve looping the existing 138 kV line into the new Stanton East switching station. This work will involve relocating one wood H-frame and the addition of two self supporting lattice steel tower structures, and the installation of approximately 400' linear feet of 795 ACSR to the new station dead end structure. | 2007-10-01 | 2007-12-14 | 2007-12-14 | 335000 |  |  |  | 100 | 138 | na | 0.2 | 795 kcmil ACSR | Steel Towers | 140 | 0.2 | na | na | 25.101(c)(5)(A) |  | 335000 | 0 | 335000 |  |  | 55 | 335000 | 0 | 0
06T62202 WB/JM | Decordova-Decordova Dam 138 kV: Reconductor with 959.6 ACSS | City of Granbury, Hood County | The Project consists of reconductoring the existing Decordova-Decordova Dam 138 kV transmission line. Two new E3A towers will be required along with raising 2 tangent towers and moving one super long span tower. New AGS units and compression Deadends will be installed. New installation will be designed and built to 138 kV standards. The existing 138 kV line currently consists of tangent lattice towers with two circuits of 795 ACSR and two (2) 3/8” EHS overhead shield wires. One circuit of the 795 ACSR will be removed. The new construction will consist of the installation of a single circuit of new 959.6 ACSS/TW and a section approximately 3,200’ in length of line over Lake Granbury will have a second 804.5 ACSR installed to create a 2-conductor bundle. | 2007-08-27 | 2007-11-04 | 2007-11-04 | 1047782 |  |  |  | 100 | 138 | na | 3.3 | 959.6 kcmil ACSS/TW, 804.5 kcmil ACSR | Steel towers | 50 | 3.3 | na | na | 25.101(c)(5)(B) |  | 1047782 | 0 | 1047782 |  |  | 56 | 1047782 | 0 | 0
05T61023 WB/JM | Martin Lake-Elkton and Martin Lake-Tri-Corner 345 kV double Circuit tower line Relocate for Grande Blvd. | City of Tyler, Smith County | This Project is in response to a request by the City of Tyler to relocate the existing 345 kV facilities to accommodate the 2nd phase of Grande Boulevard Road Extension. This project will consist of removing four (4) existing 345 kV Lattice Structures and the installation of five (5) new double circuit 345 kV single poles. The existing 345 kV line will remain in its existing centerline. The new single pole structures will be re-spanned along the existing centerline to accommodate the new roadway. No new Right of Way will be required. | 2007-08-20 | 2007-11-03 | 2007-11-03 | 998097.25 |  |  |  | 100 | 345 | na | 0.76 | 1590 kcmil ACSR | Steel towers and poles | 150 | 0.76 | na | na | 25.101(c)(5)(F) | All associated project costs will be reimbursed by the City of Tyler. | 998097.25 | 0 | 998097.25 |  |  | 57 | 998097.25 | 0 | 0
07T61013 WB/JM | Trinidad-Overton 138kV: Relocate for Grande Blvd. | City of Tyler, Smith County | This project is in response to a request by the City of Tyler to relocate a section of the Trinidad - Overton 138 kV line section from structure #48/9 to 49/7. The City of Tyler is in planning to begin their construction of Phase II extension of Grande Boulevard in the Fall of 2007.This project will involve removing ten (10) existing wood "H" frame structures and installing seventeen (17) steel self supporting single pole structures. The existing 1750 AAC will be removed and replaced with 1590 ACSR. All new poles will be installed within the existing 138 kV easement or fee owned property. As part of the roadway construction the City of Tyler will be purchasing the existing fee owned property from Oncor and will be granting Oncor an easement for the existing line on this property. The City of Tyler and Oncor signed a relocation agreement for this work in May of 2007. | 2007-09-24 | 2007-12-14 | 2007-12-14 | 1591165 |  |  |  | 100 | 138 | na | 0.78 | 1750 kcmil AAC, 1590 kcmil ACSR | Steel Poles | 100 | 0.78 | na | na | 25.101(c)(5)(F) | All associated project costs will be reimbursed by the City of Tyler. | 1591165 | 0 | 1591165 |  |  | 58 | 1591165 | 0 | 0
07J64002 WB/JM | Grande Temporary for 345 kV Martin Lake – Elkton Circuit | City of Tyler, Smith County | This is for the 345 kV temporary by-pass line section for the Martin Lake – Elkton 345 kV Circuit. The by-pass is being constructed in order to allow for the reconstruction of an approximate .5 mile section of the Martin Lake-Elkton and Martin Lake-Tri-Corner 345 kV double Circuit tower line. | 2007-08-20 | 2007-11-12 |  | 1000000 |  |  |  | 100 | 345 | na | 0..98 | 1590 kcmil ACSR | Steel Towers and Steel Poles | 150 | 0.98 | na | na | 25.101(c)(5)(F) | All associated project costs will be reimbursed by the City of Tyler. | 1000000 | 0 | 1000000 |  |  | 59 | 1000000 | 0 | 0
07T61001 SEI/BW | Brownwood-Blanket 69kv:Relocate Structures 46/14, 46/15, 46/16 & 46/17 | City of Brownwood, Brown County | Replace single circuit wood poles with single circuit wood and concrete poles with direct embed foundations. | 2008-06-01 | 2008-07-31 |  | 148699 |  |  |  | 0 | 69 | na | 0.3161 | 3/8-7 EHS Shield, 4/0 ACSR | Single Wood and Concrete Poles | Centerline Easement | 0.3161 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 148699 | 0 | 148699 |  |  | 60 | 148699 | 0 | 0
07T61010 SEI/BW | N.W. Carrollton-Gainesville 138kV:Relocate Structure 28/8 | City of Valley View, Cooke County | Replace existing wood single circuit, 5-pole deadend structure with new wood single circuit, 5-pole deadend structure with direct embed foundations. | 2007-09-06 | 2007-09-08 | 2007-09-08 | 101126 | 101126 |  |  | 100 | 138 | na | 0.14356 | 3/8-7 EHS Shield, 795 kcmil ACSR | 5-Pole Wood Deadend Structure | 100 | 0.14356 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 101126 | 0 | 101126 |  |  | 61 | 101126 | 0 | 0
07T62096 SEI/JO | White Settlement-Lockheed 69KV: Lockheed North POI | City of Fort Worth, Tarrant County | Provide a POI for a new Lockheed substation which is going to be located on the north side of their property. The circuit will be on single circuit steel poles up to the new substation location. | 2007-07-09 | 2007-08-26 | 2007-08-26 | 595000 | 595000 | 262780 |  | 100 | 69 | na | na | 795 kcmil ACSR | Steel Pole Single Circuit Structures | na | na | 50 | 0.7 | 25.101(c)(5)(A) | Final cost reported FEB 08 will remove in MAR 08 | 595000 | 595000 | 0 |  |  | 62 | 595000 | 0 | 0
07T61006 BJP/BW | E. Levee-Amelia St. 138 kV Line: DART NW1-B Relocation @ Market Center | City of Dallas, Dallas County | This project consists of relocating three self-supporting steel poles - structures T225, T226 and T227 - in order to accommodate DART's proposed NW1-B railway project at Market Center. | 2007-11-26 | 2008-01-04 |  | 185000 |  |  |  | 100 | 138 | na | 0.3 | 795 kcmil ACSR | Steel Pole | na | na | na | na | 25.101(c)(5)(F) | The existing transmission line is in DART right-of-way and will remain in DART right-of-way after the relocation. This project is 100% reimbursable. | 185000 | 0 | 185000 |  |  | 63 | 185000 | 0 | 0
07T64064 JO/RC | Sandow (Alcoa) Substation - Sandow Switch Station 138 kV: Install second 3000A circuit | Milam County | Construct a second 138 kV 3000A circuit from Sandow (Alcoa) Substation to Sandow Switch Station to accommodate the expansion of the Sandow Switch Station and connect Sandow 5. | 2007-10-15 | 2008-03-10 |  | 1223000 | 1180000 |  |  | 60 | na | 138 | 0.87 | Bundled 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.87 | na | na | 25.101(c)(5)(C) |  | 1180000 | 0 | 1180000 |  |  | 64 | 1180000 | 0 | 0
07T64065 JO/RC | Sandow (Alcoa) Substation - Sandow Switch Station 138 kV Circuit #1: Relocate and Terminate at Sandow Switch Station | Milam County | Relocate and terminate the existing 138 kV 3000A circuit (Ckt. #1) from Sandow (Alcoa) Substation to Sandow Switch Station into a different bay at Sandow Switch Station to accommodate the expansion of the Sandow Switch Station and connect Sandow 5. | 2007-10-08 | 2008-03-18 |  | 452000 | 434000 |  |  | 95 | 138 | na | 0.08 | Bundled 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.08 | na | na | 25.101(c)(5)(B) |  | 434000 | 0 | 434000 |  |  | 65 | 434000 | 0 | 0
07T64066 JO/RC | Sandow SES Substation – Minerva Substation 138 kV: Cut-in and Terminate at Sandow Switch Station | Milam County | Cut-in the existing Sandow SES Substation – Minerva Substation 138 kV line into the Sandow Switch Station. Remove structures and wires from the cut-in location at Sandow Switch Station to the Sandow SES Substation to accommodate the expansion of the Sandow Switch Station and connect Sandow 5. | 2007-12-17 | 2008-03-07 |  | 385000 | 250000 |  |  | 40 | 138 | na | 0.03 | 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.03 | na | na | 25.101(c)(5)(B) |  | 250000 | 0 | 250000 |  |  | 66 | 250000 | 0 | 0
07T64070 JO/RC | Elgin Switch – Sandow SES 138 kV: Cut-in and Terminate at Sandow Switch Station | Milam County | Cut-in the existing Elgin Switch – Sandow SES 138 kV line into the Sandow Switch Station. Remove structures and wires from the cut-in location at Sandow Switch Station to the Sandow SES Substation to accommodate the expansion of the Sandow Switch Station and connect Sandow 5. | 2008-02-04 | 2008-03-15 |  | 362000 | 321000 |  |  | 40 | 138 | na | 0.11 | 1926.9 kcmil ACSS/TW | Steel Poles | 100 | 0.11 | na | na | 25.101(c)(5)(B) |  | 321000 | 0 | 321000 |  |  | 67 | 321000 | 0 | 0
07T64071 JO/RC | Sandow Autotransformer #1 - Sandow Switch Station 138 kV: Install 3000A Circuit | Milam County | Construct a new 138 kV tie line (3000A circuit) between the Sandow Autotransformer #1 and Sandow Switch Station to accommodate the expansion of the Sandow Switch Station and connect Sandow 5. | 2008-06-02 | 2008-08-29 |  | 1320000 | 1200000 |  |  | 0 | na | 138 | 0.78 | Bundled 959.6 kcmil ACSS/TW | Steel Poles | 100 | 0.78 | na | na | 25.101(c)(5)(C) |  | 1200000 | 0 | 1200000 |  |  | 68 | 1200000 | 0 | 0
07T61019 BJP/BW | Lomo Alto 138 kV Tap Line: DART NW1-B Relocation @ Lucas Dr. | City of Dallas, Dallas County | This project consists of relocating, and raising in height, three self-supporting steel poles - structures T301, T302 and T303 - in order to accommodate DART's proposed NW1-B railway project at Lucas Drive. | 2007-11-26 | 2008-01-04 |  | 190000 |  |  |  | 100 | 138 | na | 0.33 | 795 kcmil ACSR | Steel Pole | na | na | na | na | 25.101(c)(5)(F) | Relocation is at the request of Dallas Area Rapid Transit (DART) and is 100% reimbursable by DART. | 190000 | 0 | 190000 |  |  | 69 | 190000 | 0 | 0
07T65125 MK | Jenkins-Royse City-Commerce 69 kV Line | City of Greenville, Hunt County Texas | This project consists of removing three (3) wood poles, installing two (2) wood poles and transferring conductors and shield wires in order to accommodate Texas Department of Transportation's proposed road modifications for Highway 380 near Highway 69 in Greenville Texas. | 2008-02-15 | 2008-02-29 |  | 36000 |  |  |  | 0 | 69 | na | 0.2 | 336.4 kcmil ACSR | Wood Poles | na | na | na | na | 25.101(c)(5)(F) | This project is non-reimbursable due to being in public right of way. | 36000 | 0 | 36000 |  |  | 70 | 36000 | 0 | 0
07T61007 BW/JM | Watermill-Parkdale 138 kV: Relocate for Wintergreen Road widening | City of Hutchins, Dallas County | Dallas County is widening Wintergreen Road and installing an overpass bridge in the location of the Wilmer-Parkdale 138 kV transmission line crossing. Two new steel poles will be required to raise the Watermill-Parkdale transmission line to go over the bridge. The total length of this project is approximately 1000'. Dallas County will reimburse the cost of this project. | 2008-02-06 | 2008-02-15 |  | 301809 |  |  |  | 30 | 138 | na | 0.19 | 1431 kcmil ACSR | Steel poles | 50 | 0.19 | na | na | 25.101(c)(5)(F) | This project is 100% reimbursable. | 301809 | 0 | 301809 |  |  | 71 | 301809 | 0 | 0
07T61009 BW/JM | Sandow-Minerva 138 kV: Relocate for SH6 widening near Hearne | City of Hearne, Robertson County | TXDOT is widening SH6 which will impact the Sandow-Minerva transmission line pole location. One direct embed steel pole will require relocation. A new 5' longer pole bottom section will be purchased and the existing steel pole top section will be reused. | 2008-03-15 | 2008-04-01 |  | 86019 |  |  |  | 0 | 138 | na | 0.1 | 795 kcmil ACSR | Steel poles | 50 | 0.17 | na | na | 25.101(c)(5)(F) | This project is 100% reimbursable. | 86019 | 0 | 86019 |  |  | 72 | 86019 | 0 | 0
07T61017 BW/JM | Sandow SES -Taylor relocate for US 79 near Taylor, TX | City of Taylor, Williamson County | TXDOT is widening US79 which will impact the Sandow SES-Taylor transmission line pole location. One - three wood pole angle structure will require relocation and one- wood pole H-frame will require relocation. They will be replaced with a three-pole direct embed concrete structure and a direct embed concrete H-frame structure. | 2008-04-01 | 2008-04-15 |  | 450266 |  |  |  | 0 | 138 | na | 0.1 | 795 kcmil ACSR | Wood and Concrete H Frames | 100 | 0.1 | na | na | 25.101(c)(5)(F) | This project is 100% reimbursable. | 450266 | 0 | 450266 |  |  | 73 | 450266 | 0 | 0
07T63059 JO/JM | Morgan Creek-Odessa :345 kV wirework for Long Shore Switch Station | Howard County | This project covers the wirework to terminate the Morgan Creek-Odessa EHV 345 kV line at the proposed Long Shore Switching Station. The affected line section is approximately 1200' in length of two (2) circuits of lattice towers supporting bundled 795 ACSR "Drake". The final build will include installing twelve (12) new dead end insulator assemblies and associated jumpers at the newly erected Long Shore Switching Station dead ends. | 2008-02-18 | 2/31/2008 |  | 97677 |  |  |  | 0 | 345 | na | 0.22 | Double Circuit Bundled 795 kcmil ACSR | Lattice Towers | 150 | 0.22 | na | na | 25.101(c)(5)(A) |  | 97677 | 0 | 97677 |  |  | 74 | 97677 | 0 | 0
07T62113 BW/KL | North Main – Duvall 69kV Structure #582 Relocation for TXDOT | City of Fort Worth, Tarrant County | The Texas Department of Transportation is expanding Rosedale near US 287. However, Oncor has a structure in TXDOT'S planned ROW. To accommodate the expansion of Rosedale, Oncor will relocate the structure approximately 40' south. | 2007-12-17 | 2007-12-21 |  | 31360 |  |  |  | 100 | 69 | na | na | Double Circuit 300 kcmil ACSR | Lattice Towers | Public Property | na | na | na | 25.101(c)(5)(F) | Relocation is being done at the request of the Texas Department of Transportation. Project is non-reimbursable. | 31360 | 0 | 31360 |  |  | 73 | 31360 | 0 | 0
06T64097 WB/RG | Temple Pecan Creek-Lake Creek 138 kV: Rebuild | City of Temple, Bell County, Falls County, McLennan County, City of Waco | Rebuild the 28.5 mile Temple Pecan Creek-Lake Creek 138 kV Line with 1590 kcmil ACSR on new double circuit steel and concrete pole structures with one circuit in place. | 2007-11-12 | 2008-06-01 |  | 19167955 | 16000000 |  |  | 30 | 138 | na | 28.5 | 1590 kcmil ACSR | Steel and Concrete Poles | 100 | 28.5 | na | na | 25.101(c)(5)(B) |  | 16000000 | 0 | 16000000 |  |  | 74 | 16000000 | 0 | 0
07T63061 JM/WB | Graham-Sweetwater Cogen 345kV Line- Wirework for Long Creek Switching Station | Shackelford County | This project covers the wirework to terminate the Mulberry Creek-Graham and the Graham-Sweetwater Cogen 345kV circuits on new deadend structures in the Long Creek Switching Station Addition. | 2007-11-05 | 2007-11-29 | 2007-11-29 | 120000 |  |  |  | 100 | 345 | na | na | Double Circuit Bundled 795 kcmil ACSR | Steel Deadend Structures | na | na | na | na | 25.101(c)(5)(A) |  | 120000 | 0 | 120000 |  |  | 75 | 120000 | 0 | 0
07T61011 BJP/BW | Parkdale-Lake Hubbard 138 kV Line: DART SE-2 Relocation | City of Dallas, Dallas County | This project consists of relocating, and raising in height, two steel lattice angle towers - structures T521 and T522 - in order to accommodate DART's proposed SE-2 railway project near the Parkdale Plant. | 2007-12-10 | 2008-02-01 |  | 512000 |  |  |  | 100 | 138 | na | 0.3 | 1431 kcmil ACSR | Lattice Tower | na | na | na | na | 25.101(c)(5)(F) | Relocation is at the request of Dallas Area Rapid Transit (DART) and is 100% reimbursable by DART. | 512000 | 0 | 512000 |  |  | 76 | 512000 | 0 | 0
07T62092 SEI/JO | Eagle Mountain-Saginaw 138kv:Energy Transfer POI | City of Fort Worth, Tarrant County | Install (1) new steel vertical switch structure(1/5A), install (1) new steel 3-pole DE structure(1/5B,C&D) and install (1) new concrete H-frame structure(1/5H). | 2007-11-13 | 2007-12-14 | 2007-12-14 | 688841 |  |  |  | 100 | 138 | na | 0.058902 | 795 kcmil ACSR | Steel and Concrete Poles | 100 | 0.058902 | na | na | 25.101(c)(5)(A) | Point of interconnection is at the request of Energy Transfer. | 688841 | 0 | 688841 |  |  | 77
07T65140 SEI/JO | Sulphur Springs-Edgewood 138kV:RCEC, Lake Tawakoni POI | City of Wills Point, Van Zandt County | Install (1) new steel H-frame switch structure(13/7), install (1) new Concrete 3-pole DE structure(13/7A). | 2007-12-15 | 2008-02-08 | 2008-02-08 | 507382 |  |  |  | 100 | 138 | na | 0.030682 | 795 kcmil ACSR | Steel and Concrete Poles | 100 | 0.0094697 | na | na | 25.101(c)(5)(A) | Point of interconnection is at the request of the Rayburn Country Electric Cooperative. Customer Delay | 507382 | 0 | 507382 |  |  | 78
07T63056 SEI/JO | Holt-North Andrews 138kv: XTO, University Block 9 POI | City of Andrews, Andrews County | Install (1) new steel H-frame switch structure(10/7), install (1) new Concrete 3-pole DE structure(10/7A). | 2008-02-15 | 2008-03-31 |  | 507382 |  |  |  | 0 | 138 | na | 0.025 | 795 kcmil ACSR | Steel and Concrete Poles | 100 | 0.0094697 | na | na | 25.101(c)(5)(A) | Point of interconnection is at the request of XTO. | 507382 | 0 | 507382 |  |  | 79
07T64086 SEI/JO | Trinidad-Overton 138kv: CCEC, Gwartney POI | City of Tyler, Smith County | Install (1) new steel H-frame switch structure(55/1), Install (1) new concrete H-frame structure(55/2) and install (2) new Concrete 3-pole DE structures (55/1A&B). | 2008-02-11 | 2008-03-01 |  | 566903 |  |  |  | 10 | 138 | na | 0.091288 | 795 kcmil ACSR | Steel and Concrete Poles | 100 | 0.091288 | 100 | 0.028409 | 25.101(c)(5)(A) | Point of interconnection is at the request of the Cherokee County Electric Cooperative. | 566903 | 0 | 566903 |  |  | 80
06T61030 JO | Norwood-Denton-Bowie 138kV Line - Western Extrusions | City of Carrolton, Dallas County | Relocate 138 kV line to accommodate Western Extrusion Corporation of Carrollton Texas facility expansion, this will require removing three towers and installing three angle structures and one tangent to reroute the line along the western and southern portion of Western Extrusion Corporation owned property. | 2008-02-15 | 2008-03-15 |  | 811063 |  |  |  | 0 | 138 | na | 0.19432 | 1590 kcmil ACSR | Lattice Steel Towers | 100 |  | 100 | 0.26515 | 25.101(c)(5)(D) | All associated project costs will be reimbursed by Western Extrusion Corp. 100% Reimbursable. | 811063 | 0 | 811063 |  |  | 81 | 811063 | 0 | 0
07T61022 BJP/BW | Royse-NW Carrollton 345 kV Line: DART NW-4 Relocation | City of Carrollton, Denton County | This project consists of relocating, and raising in height, two steel lattice towers - structures 40/2 and 40/3 - in order to accommodate DART's proposed NW-4 railway project at Trade Center Drive east of NW Carrollton Substation. | 2008-01-15 | 2008-02-29 |  | 250000 |  |  |  | 75 | 345 | na | 0.5 | 1590 Kcmil ACSR Bundled | Lattice Steel Tower | na | na | na | na | 25.101(c)(5)(F) | Relocation is at the request of Dallas Area Rapid Transit (DART) and is 100% reimbursable by DART. | 250000 | 0 | 250000 |  |  |  | 250000 | 0 | 0
07T65163 SEI/JO | Collin-Payne 138kV: Celina Southeast Substation Connection Upgrade | City of Celina, Collin County | Replace two (2) existing Wood single circuit H-frame structures with one 3-pole concrete angle structure and one concrete H-frame J structure, for connection to new substation dead ends. | 2008-01-23 | 2008-01-25 |  | 115424 |  |  |  | 100 | 138 | na | 0.29148 | 795 kcmil ACSR | Concrete Poles | 100 | na | na | na | 25.101(c)(5)(A) |  | 115424 | 0 | 115424
04T64156 EH/RC | Seaton - Poage 69 kV Rebuild | City of Temple, City of Belton Bell County | Rebuild 11.9 mile Seaton - Poage 69 kV line with a conductor with a minimum rating of 897 amperes. Construct for 138 kV but operate at 69 kV. | 2008-03-01 | 2008-05-15 |  | 8794000 |  |  |  | 0 | 69 | 69 | 11.9 | 795 kcmil ACSR | Steel Poles | 60 | 11.9 | na | na | 25.101(c)(5)(B) |  | 8794000 | 0 | 8794000 |  |  |  | 8794000 | 0 | 0
07T65166 JF | Royse City - Commerce 69kV line: 29/1 Relocation | City of Royse City, Rockwall County | Royse City is widening N. Houston Street and structure 29/1, necessitating its relocation. Structure 29/1 will be moved 13ft to the east and out of the new roadway. | 2008-02-18 | 2008-03-15 |  | 12000 | 12000 |  |  | 0 | 69 | na | na | 336 kcmil ACSR | Wood Pole | 45 | 0.21212 | na | na | 25.101(c)(5)(F) |  | 12000 | 0 | 12000 |  |  |  | 12000 | 0 | 0
07T61020 SEI/BW | Grapevine Jct.-Coppell Sect. 138kv:Grapevine Mills at S.H. 121 | City of Grapevine, Dallas County | Replace seven (7) existing steel double circuit structures with seven (7) new steel double circuit structures(19/6, 19/7, 19/8, 19/9, 19/10, 20/1 & 20/2). | 2008-03-10 | 2008-03-28 |  | 559472 |  |  |  | 0 | 138 | na | 1.6875 | 1033 kcmil ACSR, 795 kcmil ACSR | Steel Poles | Centerline | 0.84375 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 559472 | 0 | 559472 |  |  |  | 559472 | 0 | 0
07T61012 SEI/BW | Norwood-N.W. Carrollton 138kV: I635at I35 Relocation for TxDOT | City of Dallas, Dallas County | Replace nine (9) existing steel double circuit lattice structures with eight (8) new steel double circuit tubular structures(7/1, 7/2, 7/3, 7/4, 7/5, 7/6, 7/7 & 7/8). | 2008-04-15 | 2008-05-15 |  | 1649254 |  |  |  | 0 | 138 | na | 1.9557 | 1033 kcmil ACSR | Steel Poles | Centerline | 0.96212 | na | na | 25.101(c)(5)(F) | Relocation is at the request of the Texas Department of Transportation and is 100% reimbursable by the Texas Department of Transportation. | 1649254 | 0 | 1649254 |  |  |  | 1649254 | 0 | 0
08T63014 SEI/JO | Lamesa-Bluff Creek 138kV: Gail Substation Switch Upgrade | City of Gail, Borden County | Replace existing Wood single circuit switch structures with one (1) new steel single circuit tubular H-frame switch structure, install new switches and install one (1) new concrete 3-pole structure. | 2008-03-01 | 2008-06-15 |  | 516687 |  |  |  | 0 | 138 | na | 0.23 | 636 kcmil ACSR | Steel and Concrete | 100 | na | na | na | 25.101(c)(5)(A) |  | 516687 | 0 | 516687
08T63015 SEI/JO | Lamesa-Bluff Creek 138kV: Key Substation Switch Upgrade | City of Key, Dawson County | Replace existing Wood single circuit switch structures with one (1) new steel single circuit tubular H-frame switch structure, install new switches and install one (1) new concrete 3-pole structure. | 2008-03-01 | 2008-06-15 |  | 516687 |  |  |  | 0 | 138 | na | 0.23 | 636 kcmil ACSR | Steel and Concrete | 100 | na | na | na | 25.101(c)(5)(A) |  | 516687 | 0 | 516687
08T63016 SEI/JO | Lamesa-Bluff Creek 138kV: Sharron Ridge Substation Switch Upgrade | City of Ira, Scurry County | Replace existing Wood single circuit switch structures with one (1) new steel single circuit tubular H-frame switch structure, install new switches and install one (1) new concrete 3-pole structure. | 2008-03-01 | 2008-06-15 |  | 516687 |  |  |  | 0 | 138 | na | 0.23 | 636 kcmil ACSR | Steel and Concrete | 100 | na | na | na | 25.101(c)(5)(A) | Remove Project from MAR 08 Rpt Existing switches meet rating. | 516687 | 0 | 516687
08T63017 SEI/JO | Lamesa-N. Andrews 138kV: Paul Davis Substation Switch Upgrade | City of Tarzan, Martin County | Replace existing Wood single circuit switch structures with one (1) new steel single circuit tubular H-frame switch structure, install new switches and install one (1) new concrete 3-pole structure. | 2008-03-01 | 2008-06-15 |  | 516687 |  |  |  | 0 | 138 | na | 0.23 | 636 kcmil ACSR | Steel and Concrete | 100 | na | na | na | 25.101(c)(5)(A) |  | 516687 | 0 | 516687
08T63018 SEI/JO | Lamesa-Bluff Creek 138kV: Willow Valley Transmission to Substation Connection Upgrade | City of Gail, Borden County | Replace two (2) existing Wood single circuit H-frame structures with two (2) new wood single circuit 3-pole angle structures, for connection to new substation dead ends. | 2008-02-18 | 2008-03-31 |  | 136393 |  |  |  | 0 | 138 | na | 0.23 | 636 kcmil ACSR | Steel and Concrete | 100 | na | na | na | 25.101(c)(5)(A) |  | 136393 | 0 | 136393 |  |  | 90
07T63067 KBL | Lamesa - N. Andrews 138kV: Switch Upgrade at Mustang | Andrews County, Texas | The existing line switches at Mustang are rated 600A. To maintain grid reliability, the switches will be upgraded to 2000A. The structure holding the switches will also be replaced with a steel H-Frame. The two adjacent frames are to be replaced with concrete H-Frames | 2008-02-29 | 2008-04-15 |  | 350000 |  |  |  | 0 | 138 | na | 0.3 | 556 kcmil ACSR | Steel and Concrete H-Frames | na | na | na | na | 25.101(c)(5)(B) | Line and substation are on University of Texas Lands - Easement 7126 | 350000 | 0 | 350000 |  |  | 91
07T65168 KBL | Euless - Liggett 138kV: Connect line to Substation Dead Ends | City of Irving, Dallas County | Remove 2 concrete H-Frames from the Euless - Liggett line and connect conductor to substation dead ends. This is for the new 47MVA transformer at station 3. | 2008-03-01 | 2008-04-01 |  | 51000 |  |  |  | 0 | 138 | na | 0.02 | 1033 kcmil ACSR, Bundled | Steel A-Frames and Concrete H-Frames | na | na | na | na | 25.101(c)(5)(A) | Work is being done at Liggett Switch, Station 3 | 51000 | 0 | 51000 |  |  | 92
07T63060 WB/JM 07T63043 WB/JM | Forsan Tap 138 kV: install fiber for Drumright Morgan Creek-Spraberry 138 kV line: install fiber for Drumright | Glasscock County, Texas | Install fiber optic ground wire to support the Drumright point of interconnect for Ocotillo Wind Power. FORSAN TAP 138 KV: This line is 2 miles of single circuit "H" frame type structures. Install approximately 10,000' of OPGW below the conductors. Other work includes the installation of 2 self supporting concrete poles, replacement of 8 poles in the existing "H" frame line and the replacement of cross arms and braces on approximately 10 other structures. MORGAN CREEK TO SPRAYBERRY 138KV LINE: This existing line is 8 miles of single circuit "H" frame type structures. Replace approximately 45,000' of 3/8" EHS shield wire with OPGW. Other work includes the replacement of 11 poles. | 2008-02-25 | 2008-04-15 |  | 825139 |  |  |  | 0 | 138 | na | 11.36 | .546, diameter 24 count fiber OPGW | Wood H-frames | 100 | 11.36 | na | na | 25.101(c)(5)(B) |  | 825139 | 0 | 825139 |  |  | 93 | 825139 | 0 | 0
07T65159 WB/JM | Northlake-Morrison 138kV; Tap Line for Irving LBJ Transformer | City of Irving Dallas County, Texas | This project is in response to the addition of an transformer in the Irving LBJ substation. Work will include installing one double circuit dead end and tapping the existing North Lake - Morrison 138 kv Line for the additional substation facilities. One new steel pole will be installed. No additional ROW will be required | 2008-03-01 | 2008-04-15 |  | 97000 |  |  |  | 0 | 138 | na | 0.1 | Double Circuit Single 1033 kcmil ACSR | Steel poles | 100 | 0.1 | na | na | 25.101(c)(5)(A) |  | 97000 | 0 | 97000 |  |  | 94 | 97000 | 0 | 0
08T64012 JF | Temple - Taylor 69kV: Little River Substation Expansion | City of Little River Bell County | Expansion of Little River substation requires that two (2) deadend structure be installed in the substation and three (3) wooden poles outside of the substation will be replaced with concrete poles | 2008-03-15 | 2008-04-15 |  | 343000 |  |  |  | 0 | 69 | na | 0.2 | 795 kcmil ACSR | Steel or Concrete Poles | na | na | na | na | 25.101(c)(5)(A) |  | 343000 | 0 | 343000 |  |  | 95 | 343000 | 0 | 0
08T64013 JF | Elkton - Edgewood 138kV: Tyler Southwest Substation | City of Tyler, Smith County | New Oncor Tyler Southwest substation requires three (3) deadend single pole structures and six (6) single tap pole structures to loop into the station | 2008-03-15 | 2008-04-15 |  | 80000 |  |  |  | 0 | 138 | na | 0.2 | 636 kcmil ACSR | Steel or Concrete Poles | na | na | na | na | 25.101(c)(5)(A) |  | 80000 | 0 | 80000 |  |  |  | 80000 | 0 | 0
08T65026 JF | Valley - Paris 138kV: FCEC Bonham Lake POI | Fannin County | New FCEC Bonham Lake substation requires an H-frame switch structure to tap into the station | 2008-03-15 | 2008-04-15 |  | 500000 |  |  |  | 0 | 138 | na | 0.1 | 795 kcmil ACSR | Steel H-Frame Switch Structure | 100 | 0.1 | na | na | 25.101(c)(5)(A) |  | 500000 | 0 | 500000 |  |  | 96 | 500000 | 0 | 0
06T62209 JF/WB | Sherry-International-Liggett 138kV: Connect Executive Parkway sub | City of Arlington, Tarrant County, Texas | Scope of work includes looping the double circuit 138kV Sherry-International Airport-Liggett and Sherry - Handley Lines into the new Arlington Executive Parkway substation. The substation will be located west of existing structure number 3/10. | 2008-03-01 | 2008-12-15 |  | 1130000 |  |  |  | 0 | 138 | na | 0.3 | 1926.9 kcmil ACSS/TW | Steel Poles | na | na | 75 | 0.15 | 25.101(c)(5)(A) |  | 1130000 | 0 | 1130000 |  |  | 97 | 1130000 | 0 | 0
07T61023 JM/BW | Elkton - Jacksonville 138 kV: Relocate "H" Frames for Developer | City of Tyler, Smith County Texas | The project consists of relocating an existing wood "H" frame for a developer. The existing wood structure will be replaced with a new concrete "H" frame installed approximately 75' from the existing structure outside of the proposed roadway. | 2008-03-01 | 2008-10-01 |  | 88415 |  |  |  | 0 | 138 | na | 0.01 | 336.4 kcmil ACSR Bundled | Wood/Concrete "H" frames | 100 | 0.01 | na | na | 25.101(c)(5)(D) | All associated project cost will be reimbursed to ONCOR by the developer. | 88415 | 0 | 88415 |  |  | 98 | 88415 | 0 | 0
08T65054 SEI/JO | Collin-Colony 138kV: Roman Juarez (Brazos) POI | City of Frisco, Collin County | Replace two (2) existing steel double circuit structures (Str. 27/7 & 27/8) with one (1) new steel double circuit 115' A.G. structure. | 2008-05-01 | 2008-05-15 |  | 154075 |  |  |  |  | 138 | na | 0.34375 | 1590 kcmil ACSR | One (1) new steel double circuit single pole structure. | 100 | 0.34375 | na | na | 25.101(c)(5)(A) | Point of interconnection is at the request of the Brazos Electric Cooperative. | 154075 | 0 | 154075 |  |  | 99 |  |  |  |  | COPY OF CLOSED OUT PROJECTS INCLUDING VALUES
08T61008 BJP/BW | Denton Dr.-Greenville-Lakemont Tap 138 kV Line: DART NW-3 Relocation | City of Dallas, Dallas County | This project consists of relocating, and raising in height, five steel narrow-base lattice towers - structures T221 thru T225 - in order to accommodate DART's proposed NW-3 railway project near the intersection of Northwest Highway and Harry Hines Boulevard. | 2008-03-31 | 2008-05-30 |  | 425005 |  |  |  |  | 138 | na | 1.3 | Double Ckt. 477kcmil ACSR | Lattice Steel Tower | na | na | na | na | 25.101(c)(5)(F) | Relocation is at the request of Dallas Area Rapid Transit (DART) and is 100% reimbursable by DART. | 425005 | 0 | 425005 |  |  | 100 |  |  |  | NO PROJECTS WERE CLOSED OUT FOR JANUARY 2008 REPORT
08T64028 EH/RC | Relocate Str. 3/4 on Temple Switch-Killeen 345 kV | Bell County | Relocate and raise Str. 3/4 on Temple Switch-Killeen 345 kV for Seaton-Poage Rebuild Project | 2008-04-01 | 2008-05-15 |  | 94000 |  |  |  |  | 345 | 345 | 0 | 795 kcmil ACSR bundled | Lattice Tower | 150 | 37.4 | na | na | 25.101(c)(5)(B) | INTERIM REPORT FEBRUARY 19 2008 | 94000 | 0 | 94000
08T64029 EH/RC | Relocate Str. 35/2 on Lake Creek-Sandow 345 138 kV | Bell County | Relocate and raise Str. 35/2 on Lake Creek-Sandow 345 kV for Seaton-Poage Rebuild Project | 2008-04-01 | 2008-05-15 |  | 106000 |  |  |  |  | 345 | 345 | 0 | 795 kcmil ACSR bundled | Lattice Tower | 150 | 37.4 | na | na | 25.101(c)(5)(B) | INTERIM REPORT FEBRUARY 19 2008 | 106000 | 0 | 106000
08T64030 EH/RC | Relocate Str. 38/4 on Sandow-Temple 138 kV | Bell County | Relocate and raise Str. 38/4 on Sandow-Temple 138 kV for Seaton-Poage Rebuild Project | 2008-04-01 | 2008-05-15 |  | 75000 |  |  |  |  | 138 | 138 | 0 | 795 kcmil ACSR | Steel Pole | 100 | 38.8 | na | na | 25.101(c)(5)(B) | INTERIM REPORT FEBRUARY 19 2008 | 75000 | 0 | 75000
| CCN APPLICATIONS - APPROVED | [21 empty] | 0 | 0 | 0 |  |  | 102
04T64042, 07T64062 BW/RG | Copperas Cove-Ding Dong 138 kV: Construct New Line | Bell County, Coryell County | Construct 15.7 miles 138 kV single circuit single pole from Oncor Electric Delivery Copperas Cove Substation to BEPC's Ding Dong Substation. Rebuild 7 poles exiting the Copperas Cove Substation on existing Oncor easement during the fall of 2005 to accommodate a request by Oncor Electric Delivery Distribution. | 2008-02-11 | 2008-06-01 |  | 7145776 | 8389700 |  |  | 1 | na | 138 | 15.7 | 795 kcmil ACSS | Steel and/or Concrete Poles | na | na | 70 | 15.7 | 27179 | Application filed 12/31/02. Application approved 01/29/2004. This project is to be completed in phases. | 8389700 | 0 | 8389700 |  |  | 103
06T65281 DRC | West Levee-Norwood 345 kV Line | City of Dallas, Dallas County | Construct 345 kV double-circuit line from West Levee Switch to junction point with the Norwood-NW Carrollton 345 kV line with one circuit installed initially and the 2nd circuit to be installed later as needed. The portion from the junction point with the Norwood-NW Carrollton 345 kV Line and Norwood Switch will use the vacant circuit position on double-circuit poles which has already been certificated. Approximately 0.7 miles will be underground. | 2009-04-01 | 2009-12-31 |  | 18100000 |  |  |  | 0 | na | 345 | 6.5 | 1590 kcmil ACSR Bundled, UG Cable | Double-circuit Steel Poles | na | na | 100 | 6.5 | 32455 | Application filed 3/10/2006. Final Order issued 6/07/07. | 18100000 | 0 | 18100000 |  |  | 104 | 18100000 | 0 | 0
07T62122 EH/JM | Elizabeth Creek -Roanoke 138kV New Double Circuit 1590 line to Elizabeth Creek | Denton County, Texas | This project is to construct the Roanoke - Elizabeth Creek 138 kV line. This line will be 3.24 miles of double circuit utilizing approximately 18 double circuit steel tangent poles, 7 double circuit steel deadend poles, 6 swinging angle steel poles, 2 single circuit steel tangent poles, 2 single circuit steel dead end poles | 2008-03-03 | 2008-05-15 |  | 3995649.46 |  |  |  | 0 | na | 138 kV | 3.24 | 1590 kcmil ACSR | Steel poles | Varies 60' & 70' | 3.24 | na | na | 17686 | Application Filed 07/14/1997 Final Order Issued 04/01/1998 Moved listing to CCN section | 3995649.46 | 0 | 3995649.46 |  |  | 105 | 3995649.46 | 0 | 0
| CCN APPLICATIONS - PENDING | [21 empty] | 0 | 0 | 0 |  |  | 106
05T64079 | Salado - Hutto 345kV Construct New Line | Bell County, Williamson County | Construct a 345kV double-circuit line from Salado Switch Station to Hutto Switch Station with two (2) circuits installed. | 2008-11-01 | 2010-05-15 |  | 70100000 |  |  |  | 0 | na | 345 | 36.4 | 1590 kcmil ACSR Bundled | Double Circuit Steel Poles and Steel Lattice Towers | na | na | 160 | 36.4 | 34440 | Application Filed 7/10/2007. | 70100000 | 0 | 70100000 |  |  | 107 | 70100000 | 0 | 0
COMPLETED PROJECTS REMOVED FROM 1/15/2008 REPORT. (NONE)
5 NEW PROJECTS: | 854080
[34 empty] | 0 | 0
122
130
131
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
|  | NEW PROJECTS: | 2215893
6
0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 27956105 | 15889212 | 223967207.09 | 239856419.09
[24 empty] | 9 | 101 | 110 | Project Count
[24 empty] | Completed | Active | Total
Note on A109: Allen Steven Boling: PUC STAFF: THIS PROJECT NUMBER WAS CHANGED IN SOME SUBTLE WAY, AND IS NOT IDENTICAL TO THE PREVIOUS MONTH.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on I1: aboling: Please enter only a single integer, if possible.
Note on J26: Allen Steven Boling: ENTERED COST OF $0.00001 TO APPROXIMATE NO-COST CLOSEOUT OF THIS PROJECT AND ALLOW DETECTION BY "COMPLETED PROJECTS" CELLS.
Note on J31: Allen Steven Boling: ENTERED COST OF $0.00001 TO APPROXIMATE NO-COST CLOSEOUT OF THIS PROJECT AND ALLOW DETECTION BY "COMPLETED PROJECTS" CELLS.
Note on J32: Allen Steven Boling: ENTERED COST OF $0.00001 TO APPROXIMATE NO-COST CLOSEOUT OF THIS PROJECT AND ALLOW DETECTION BY "COMPLETED PROJECTS" CELLS.
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.
Note on AD78: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD103: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD104: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD105: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD106: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD107: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD108: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD109: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AD112: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE78: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE103: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE104: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE105: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE106: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE107: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE108: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE109: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AE112: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF78: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF103: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF104: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF105: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF106: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF107: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF108: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF109: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.
Note on AF112: Allen Steven Boling: FORMULA DELETED TO ACCOMMODATE NEW PROJECT OR CHANGED PROJECT NUMBER.

## TVEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
118006 | Scurry to Combine Transmission | Kaufman | Transmission Line to connect Scurry and Combine substations | 2006-01-01 |  |  | 1814100 | 7500000 |  |  | 45% | NA | 138 | 10 | 795MCM, 26/7, ACSR Drake | concrete monopole w/ davit arms | NA | NA | 80 | 10 | 14653 |  | 7500000 | 0 | 7500000 |  |  | 7500000 | 0 | 0
145000, 141404, & 147052 | NTMWD Tawakoni transmission | Van Zandt | Transmission Line to feed NTMWD pump station | 2007-09-01 |  |  | 954063 | 954063 |  |  | 95% | NA | 138 | 1.8 | 795MCM, 26/7, ACSR Drake | concrete monopole w/ davit arms | NA | NA | 100 | 1.8 | 33525 |  | 954063 | 0 | 954063 |  |  | 5000000 | -4045937 | -4045937
132073 & 147053 | NTMWD Combine | Kaufman | Short transmission line to feed NTMWD pump substation | 2007-09-01 |  |  | 1500000 | 1500000 |  |  | 99% | NA | 138 | 0.5 | 795MCM, 26/7, ACSR Drake | concrete monopole w/ davit arms | NA | NA | 100 | 0.5 | 25.101 (c)(5)(A) |  | 1500000 | 0 | 1500000 |  |  | 1500000 | 0 | -4045937
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A
#N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 9954063 | 9954063
[24 empty] | 0 | 3 | 3 | Project Count
[24 empty] | Completed | Active | Total
Note on H3: Allen Steven Boling: $ 954,063 T Line; $325,000 Switch and $3,342,600 Sub. Stations Subtotal non T-Line=$3,757,600 TOTAL PROJECT COST EST: $4,711,663
Note on I3: Allen Steven Boling: $ 954,063 T Line; Subtotal non T-Line=$4,045,937 TOTAL PROJECT FINAL COST EST: $5,000,000. (From T. Craig email 03/13/2008)

## WCEC
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
1A | DWU 138kV Tap 69kV Loop | Wood | Dbl ckt / sgl pole - 138kV service to DWU, 69kV loop Yantis to Cathey | 6/25/2007 ROW 8/27 Const Start |  |  | 4200000 | 6935000 |  |  | 63% | NA | 138 / 69 | 6 dbl / 2.4 sgl | 795 ACSR "Drake" | Single Pole Concrete | 80 sgl ckt | 2.4 | 100 dbl ckt | 6 | 30254 | Revise % Complete | 6935000 | 0 | 6935000 |  |  | 6935000 | 0 | 0
2A | Feed to Sand Springs Substation | Wood | Dbl ckt / sgl pole - 138kV service to Sand Springs Substation | 7/1/2008 Est. Start ROW Clr |  |  | 934111 | 0 |  |  | 0% | NA | 138 |  | 795 ACSR "Drake" | Single Pole Concrete | NA | NA | 100 |  | 32070 | Revise Est. Start Date | 934111 | 0 | 934111 |  |  | 934111 | 0 | 0
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | 0 | 0 | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 7869111 | 7869111
[24 empty] | 0 | 2 | 2 | Project Count
[24 empty] | Completed | Active | Total
Note on A2: Allen Steven Boling: STAFF ASSIGNED ARBITRARY PROJECT NUMBER TO ALLOW CHECKING IN THIS SHEET.
Note on A3: Allen Steven Boling: STAFF ASSIGNED ARBITRARY PROJECT NUMBER TO ALLOW CHECKING IN THIS SHEET.
Note on H1: aboling: Please enter only a single integer, if possible.
Note on H2: Allen Steven Boling: $4.200,000 T Line; $2,700,000 Station
Note on H3: Allen Steven Boling: $934,111 T Line; $1,931,000 Station
Note on I1: aboling: Please enter only a single integer, if possible.
Note on I2: Allen Steven Boling: $6.935,000T Line; $3,014,000 Station
Note on I3: Allen Steven Boling: $0 T Line; $0Station
Note on M1: aboling: If applicable.
Note on N1: aboling: If applicable.

## UPSHUR (hidden)
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | Project Count
[24 empty] | Completed | Active | Total

## NEW3 (hidden)
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | Project Count
[24 empty] | Completed | Active | Total

## NEW4 (hidden)
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | Project Count
[24 empty] | Completed | Active | Total

## NEW (hidden)
Utility's Project Number | Project Name | Location (City/County) | Description | Estimated (or Actual) Start Date | Finish Date (Construction Complete) | Date Energized (If Applicable) | Initial Estimated Project Cost | Final Estimated Project Cost | Final Actual Project Cost | % Variance | Percent Complete | Existing Voltage | Upgraded or New Voltage | Circuit Length (Miles) | Conductor Type & Size & Bundling | Structure Type(s) | Existing ROW Width (Feet) | Existing ROW Length (Miles) | New ROW Width (Feet) | New ROW Length (Miles) | Rule Section or PUC Control Number | Comments | INITIAL OR FINAL SELECTER | COMPLETED PROJECTS | ACTIVE PROJECTS | Estimated OR Actual Project Cost (SUBSTATION) |  | Last Month: | Current minus last month: | Cumulative Sum
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0 |  |  | #N/A | #N/A | #N/A
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | 0 | 0 | 0
[23 empty] | Actual Cost of Projects Completed This Month (Will Not Appear on Next Month Report): | Estimated Cost of Projects Completed This Month: | Estimated Cost of Projects Remaining Active This Month: | Total Estimated Cost of Projects Appearing in This Report:
[23 empty] | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | Project Count
[24 empty] | Completed | Active | Total